## limits
Human perception curves | [5 empty] | +/- 20% window
rpm | amplitude (in) |  |  |  |  | rpm |  |  |  | amplitude (in)
100 | 0.0093 | 0.0033 | 0.0012 |  |  | 2880 | 3600 | 4320 |  | 1e-09
10000 | 0.0001 | 3.3e-05 | 1e-05 |  |  | 2880 | 3600 | 4320 |  | 0.01
100000 | 1.1e-05 | 3.33e-06 | 9e-07 |  |  |  | 3600
rpm | amplitude (in) |  |  |  |  | vendor requirements
100 | 0.1 |  |  |  |  | 0.0001 | 0.00026526 | in | 0.0067376 | mm
2300 | 0.00055 |  |  |  |  | 100000 | 0.00026526 | in | 0.0067376 | mm
10000 | 0.00013
100000 | 1.45e-05 |  |  |  |  | velocity limit: | 2.54 | mm/sec | related amplitude y'/ w |  | 0.0067376 | mm
[7 empty] | 0.1 | in/sec |  |  | 0.00026526 | in
Machine limits
Blake 1964 | [5 empty] | Baxter & Bernhard 1967
rpm | amplitude (in) |  | rpm | amplitude (in) |  | rpm | amplitude (in)
100 | 0.0037 |  | 100 | 0.0014 |  | 100 | 0.00045 | 0.00095 | 0.00175 | 0.00375 | 0.0075
300 | 0.0024 |  | 300 | 0.0008 |  | 10000 | 4e-06 | 9.5e-06 | 1.65e-05 | 3.5e-05 | 6.5e-05
1700 | 0.0011 |  | 1700 | 0.00034 |  | 100000 | 3.55e-07 | 9.33e-07 | 1.64e-06 | 3.44e-06 | 6.2e-06
3500 | 0.0005 |  | 10000 | 6.7e-05
10000 | 0.00014 |  | 100000 | 8.18e-06
100000 | 9.33e-06 |  |  |  |  | Industry Requirments
[6 empty] | 0.0001 | 0.00027795 | in | 0.00706 | mm
service factor for machine performance |  |  |  | 1 |  | 100000 | 0.00027795 | in | 0.00706 | mm
(applied only for horizontal amplitude
of vibrations) | [5 empty] | velocity limit: | 2.6616 | mm/sec | related amplitude y'/ w |  | 0.00706 | mm
[7 empty] | 0.10479 | in/sec |  |  | 0.00027795 | in
w motor |  | 3600 | rpm | 376.9911 | rad/sec
w compressor |  | 3600 | rpm | 376.9911 | rad/sec
|  |  | frequency rpm |  |  |  |  | amplitude (in)
[5 empty] | 2880 | 3600 | 4320 | 1e-06
[5 empty] | 2880 | 3600 | 4320 | 0.01
| velocity limit for operating |  | related amplitude y'/ w |  |  |  | velocity limit for malfunction |  | related amplitude y'/ w
| 2.9 | mm/sec | 0.0076925 | mm | (22 m m ) |  | 5 | mm/sec | 0.013263 | mm | (48 m m )
| 0.11417 | in/sec | 0.00030285 | in |  |  | 0.19685 | in/sec | 0.00052216 | in

## P3_Frozen UB
Point 3: At SW Corner
Lower Bound Soil
Pump Operating = 4215 rpm
Frequency (rpm) | Amplitude (m) |  |  | Amplitude (in)
| x | y | z | x | y | z
0 | 4.75e-18 | 4.77e-19 | 3.34e-18 | 1.8701e-16 | 1.878e-17 | 1.315e-16
40 | 1.06e-10 | 9.71e-12 | 6.31e-11 | 4.1732e-09 | 3.8228e-10 | 2.4843e-09
80 | 4.32e-10 | 3.93e-11 | 2.47e-10 | 1.7008e-08 | 1.5472e-09 | 9.7244e-09
120 | 9.74e-10 | 8.86e-11 | 5.43e-10 | 3.8346e-08 | 3.4882e-09 | 2.1378e-08
160 | 1.74e-09 | 1.58e-10 | 9.46e-10 | 6.8504e-08 | 6.2205e-09 | 3.7244e-08
200 | 2.72e-09 | 2.48e-10 | 1.45e-09 | 1.0709e-07 | 9.7638e-09 | 5.7087e-08
240 | 3.95e-09 | 3.6e-10 | 2.06e-09 | 1.5551e-07 | 1.4173e-08 | 8.1102e-08
280 | 5.41e-09 | 4.94e-10 | 2.76e-09 | 2.1299e-07 | 1.9449e-08 | 1.0866e-07
320 | 7.12e-09 | 6.5e-10 | 3.55e-09 | 2.8031e-07 | 2.5591e-08 | 1.3976e-07
360 | 9.09e-09 | 8.3e-10 | 4.43e-09 | 3.5787e-07 | 3.2677e-08 | 1.7441e-07
400 | 1.13e-08 | 1.03e-09 | 5.41e-09 | 4.4488e-07 | 4.0551e-08 | 2.1299e-07
440 | 1.38e-08 | 1.26e-09 | 6.47e-09 | 5.4331e-07 | 4.9606e-08 | 2.5472e-07
480 | 1.67e-08 | 1.51e-09 | 7.61e-09 | 6.5748e-07 | 5.9449e-08 | 2.9961e-07
520 | 1.98e-08 | 1.78e-09 | 8.86e-09 | 7.7953e-07 | 7.0079e-08 | 3.4882e-07
560 | 2.32e-08 | 2.09e-09 | 1.02e-08 | 9.1339e-07 | 8.2283e-08 | 4.0157e-07
600 | 2.7e-08 | 2.41e-09 | 1.16e-08 | 1.063e-06 | 9.4882e-08 | 4.5669e-07
640 | 3.11e-08 | 2.76e-09 | 1.32e-08 | 1.2244e-06 | 1.0866e-07 | 5.1969e-07
680 | 3.56e-08 | 3.14e-09 | 1.49e-08 | 1.4016e-06 | 1.2362e-07 | 5.8661e-07
720 | 4.05e-08 | 3.55e-09 | 1.68e-08 | 1.5945e-06 | 1.3976e-07 | 6.6142e-07
760 | 4.58e-08 | 3.98e-09 | 1.88e-08 | 1.8031e-06 | 1.5669e-07 | 7.4016e-07
800 | 5.16e-08 | 4.43e-09 | 2.1e-08 | 2.0315e-06 | 1.7441e-07 | 8.2677e-07
840 | 5.78e-08 | 4.91e-09 | 2.35e-08 | 2.2756e-06 | 1.9331e-07 | 9.252e-07
880 | 6.46e-08 | 5.41e-09 | 2.62e-08 | 2.5433e-06 | 2.1299e-07 | 1.0315e-06
920 | 7.2e-08 | 5.93e-09 | 2.93e-08 | 2.8346e-06 | 2.3346e-07 | 1.1535e-06
960 | 7.99e-08 | 6.48e-09 | 3.28e-08 | 3.1457e-06 | 2.5512e-07 | 1.2913e-06
1000 | 8.85e-08 | 7.03e-09 | 3.67e-08 | 3.4843e-06 | 2.7677e-07 | 1.4449e-06
1040 | 9.78e-08 | 7.61e-09 | 4.11e-08 | 3.8504e-06 | 2.9961e-07 | 1.6181e-06
1080 | 1.08e-07 | 8.19e-09 | 4.6e-08 | 4.252e-06 | 3.2244e-07 | 1.811e-06
1120 | 1.19e-07 | 8.77e-09 | 5.13e-08 | 4.685e-06 | 3.4528e-07 | 2.0197e-06
1160 | 1.3e-07 | 9.36e-09 | 5.72e-08 | 5.1181e-06 | 3.685e-07 | 2.252e-06
1200 | 1.43e-07 | 9.94e-09 | 6.37e-08 | 5.6299e-06 | 3.9134e-07 | 2.5079e-06
1240 | 1.56e-07 | 1.05e-08 | 7.09e-08 | 6.1417e-06 | 4.1339e-07 | 2.7913e-06
1280 | 1.7e-07 | 1.11e-08 | 7.88e-08 | 6.6929e-06 | 4.3701e-07 | 3.1024e-06
1320 | 1.86e-07 | 1.16e-08 | 8.75e-08 | 7.3228e-06 | 4.5669e-07 | 3.4449e-06
1360 | 2.02e-07 | 1.2e-08 | 9.7e-08 | 7.9528e-06 | 4.7244e-07 | 3.8189e-06
1400 | 2.2e-07 | 1.25e-08 | 1.07e-07 | 8.6614e-06 | 4.9213e-07 | 4.2126e-06
1440 | 2.39e-07 | 1.29e-08 | 1.18e-07 | 9.4094e-06 | 5.0787e-07 | 4.6457e-06
1480 | 2.58e-07 | 1.32e-08 | 1.3e-07 | 1.0157e-05 | 5.1969e-07 | 5.1181e-06
1520 | 2.79e-07 | 1.34e-08 | 1.42e-07 | 1.0984e-05 | 5.2756e-07 | 5.5906e-06
1560 | 3e-07 | 1.36e-08 | 1.55e-07 | 1.1811e-05 | 5.3543e-07 | 6.1024e-06
1600 | 3.22e-07 | 1.37e-08 | 1.68e-07 | 1.2677e-05 | 5.3937e-07 | 6.6142e-06
1640 | 3.44e-07 | 1.38e-08 | 1.82e-07 | 1.3543e-05 | 5.4331e-07 | 7.1654e-06
1680 | 3.66e-07 | 1.38e-08 | 1.95e-07 | 1.4409e-05 | 5.4331e-07 | 7.6772e-06
1720 | 3.87e-07 | 1.4e-08 | 2.08e-07 | 1.5236e-05 | 5.5118e-07 | 8.189e-06
1760 | 4.06e-07 | 1.42e-08 | 2.21e-07 | 1.5984e-05 | 5.5906e-07 | 8.7008e-06
1800 | 4.24e-07 | 1.45e-08 | 2.32e-07 | 1.6693e-05 | 5.7087e-07 | 9.1339e-06
1840 | 4.39e-07 | 1.5e-08 | 2.42e-07 | 1.7283e-05 | 5.9055e-07 | 9.5276e-06
1880 | 4.52e-07 | 1.57e-08 | 2.51e-07 | 1.7795e-05 | 6.1811e-07 | 9.8819e-06
1920 | 4.61e-07 | 1.66e-08 | 2.57e-07 | 1.815e-05 | 6.5354e-07 | 1.0118e-05
1960 | 4.68e-07 | 1.77e-08 | 2.63e-07 | 1.8425e-05 | 6.9685e-07 | 1.0354e-05
2000 | 4.71e-07 | 1.89e-08 | 2.66e-07 | 1.8543e-05 | 7.4409e-07 | 1.0472e-05
2040 | 4.72e-07 | 2.02e-08 | 2.69e-07 | 1.8583e-05 | 7.9528e-07 | 1.0591e-05
2080 | 4.7e-07 | 2.15e-08 | 2.7e-07 | 1.8504e-05 | 8.4646e-07 | 1.063e-05
2120 | 4.66e-07 | 2.29e-08 | 2.69e-07 | 1.8346e-05 | 9.0157e-07 | 1.0591e-05
2160 | 4.6e-07 | 2.42e-08 | 2.69e-07 | 1.811e-05 | 9.5276e-07 | 1.0591e-05
2200 | 4.54e-07 | 2.55e-08 | 2.67e-07 | 1.7874e-05 | 1.0039e-06 | 1.0512e-05
2240 | 4.46e-07 | 2.67e-08 | 2.66e-07 | 1.7559e-05 | 1.0512e-06 | 1.0472e-05
2280 | 4.38e-07 | 2.78e-08 | 2.63e-07 | 1.7244e-05 | 1.0945e-06 | 1.0354e-05
2320 | 4.3e-07 | 2.89e-08 | 2.61e-07 | 1.6929e-05 | 1.1378e-06 | 1.0276e-05
2360 | 4.21e-07 | 2.99e-08 | 2.58e-07 | 1.6575e-05 | 1.1772e-06 | 1.0157e-05
2400 | 4.13e-07 | 3.09e-08 | 2.56e-07 | 1.626e-05 | 1.2165e-06 | 1.0079e-05
2440 | 4.05e-07 | 3.18e-08 | 2.53e-07 | 1.5945e-05 | 1.252e-06 | 9.9606e-06
2480 | 3.97e-07 | 3.28e-08 | 2.5e-07 | 1.563e-05 | 1.2913e-06 | 9.8425e-06
2520 | 3.89e-07 | 3.38e-08 | 2.46e-07 | 1.5315e-05 | 1.3307e-06 | 9.685e-06
2560 | 3.82e-07 | 3.49e-08 | 2.43e-07 | 1.5039e-05 | 1.374e-06 | 9.5669e-06
2600 | 3.76e-07 | 3.62e-08 | 2.4e-07 | 1.4803e-05 | 1.4252e-06 | 9.4488e-06
2640 | 3.71e-07 | 3.76e-08 | 2.37e-07 | 1.4606e-05 | 1.4803e-06 | 9.3307e-06
2680 | 3.66e-07 | 3.93e-08 | 2.34e-07 | 1.4409e-05 | 1.5472e-06 | 9.2126e-06
2720 | 3.62e-07 | 4.17e-08 | 2.32e-07 | 1.4252e-05 | 1.6417e-06 | 9.1339e-06
2760 | 3.59e-07 | 4.4e-08 | 2.3e-07 | 1.4134e-05 | 1.7323e-06 | 9.0551e-06
2800 | 3.58e-07 | 4.66e-08 | 2.28e-07 | 1.4094e-05 | 1.8346e-06 | 8.9764e-06
2840 | 3.57e-07 | 4.95e-08 | 2.27e-07 | 1.4055e-05 | 1.9488e-06 | 8.937e-06
2880 | 3.58e-07 | 5.28e-08 | 2.26e-07 | 1.4094e-05 | 2.0787e-06 | 8.8976e-06
2920 | 3.6e-07 | 5.65e-08 | 2.26e-07 | 1.4173e-05 | 2.2244e-06 | 8.8976e-06
2960 | 3.64e-07 | 6.05e-08 | 2.27e-07 | 1.4331e-05 | 2.3819e-06 | 8.937e-06
3000 | 3.69e-07 | 6.48e-08 | 2.29e-07 | 1.4528e-05 | 2.5512e-06 | 9.0157e-06
3040 | 3.76e-07 | 6.93e-08 | 2.31e-07 | 1.4803e-05 | 2.7283e-06 | 9.0945e-06
3080 | 3.84e-07 | 7.42e-08 | 2.35e-07 | 1.5118e-05 | 2.9213e-06 | 9.252e-06
3120 | 3.93e-07 | 7.92e-08 | 2.39e-07 | 1.5472e-05 | 3.1181e-06 | 9.4094e-06
3160 | 4.04e-07 | 8.44e-08 | 2.45e-07 | 1.5906e-05 | 3.3228e-06 | 9.6457e-06
3200 | 4.15e-07 | 8.97e-08 | 2.51e-07 | 1.6339e-05 | 3.5315e-06 | 9.8819e-06
3240 | 4.28e-07 | 9.49e-08 | 2.59e-07 | 1.685e-05 | 3.7362e-06 | 1.0197e-05
3280 | 4.41e-07 | 1e-07 | 2.68e-07 | 1.7362e-05 | 3.937e-06 | 1.0551e-05
3320 | 4.54e-07 | 1.05e-07 | 2.78e-07 | 1.7874e-05 | 4.1339e-06 | 1.0945e-05
3360 | 4.67e-07 | 1.1e-07 | 2.9e-07 | 1.8386e-05 | 4.3307e-06 | 1.1417e-05
3400 | 4.81e-07 | 1.14e-07 | 3.03e-07 | 1.8937e-05 | 4.4882e-06 | 1.1929e-05
3440 | 4.93e-07 | 1.17e-07 | 3.18e-07 | 1.9409e-05 | 4.6063e-06 | 1.252e-05
3480 | 5.05e-07 | 1.2e-07 | 3.35e-07 | 1.9882e-05 | 4.7244e-06 | 1.3189e-05
3520 | 5.16e-07 | 1.22e-07 | 3.55e-07 | 2.0315e-05 | 4.8031e-06 | 1.3976e-05
3560 | 5.26e-07 | 1.23e-07 | 3.78e-07 | 2.0709e-05 | 4.8425e-06 | 1.4882e-05
3600 | 5.34e-07 | 1.24e-07 | 4.05e-07 | 2.1024e-05 | 4.8819e-06 | 1.5945e-05
3640 | 5.41e-07 | 1.23e-07 | 4.36e-07 | 2.1299e-05 | 4.8425e-06 | 1.7165e-05
3680 | 5.47e-07 | 1.2e-07 | 4.73e-07 | 2.1535e-05 | 4.7244e-06 | 1.8622e-05
3720 | 5.51e-07 | 1.17e-07 | 5.15e-07 | 2.1693e-05 | 4.6063e-06 | 2.0276e-05
3760 | 5.55e-07 | 1.12e-07 | 5.63e-07 | 2.185e-05 | 4.4094e-06 | 2.2165e-05
3800 | 5.57e-07 | 1.06e-07 | 6.14e-07 | 2.1929e-05 | 4.1732e-06 | 2.4173e-05
3840 | 5.58e-07 | 1.01e-07 | 6.66e-07 | 2.1969e-05 | 3.9764e-06 | 2.622e-05
3880 | 5.59e-07 | 9.69e-08 | 7.13e-07 | 2.2008e-05 | 3.815e-06 | 2.8071e-05
3920 | 5.6e-07 | 9.71e-08 | 7.45e-07 | 2.2047e-05 | 3.8228e-06 | 2.9331e-05
3960 | 5.62e-07 | 1.02e-07 | 7.56e-07 | 2.2126e-05 | 4.0157e-06 | 2.9764e-05
4000 | 5.63e-07 | 1.1e-07 | 7.44e-07 | 2.2165e-05 | 4.3307e-06 | 2.9291e-05
4040 | 5.65e-07 | 1.19e-07 | 7.11e-07 | 2.2244e-05 | 4.685e-06 | 2.7992e-05
4080 | 5.66e-07 | 1.27e-07 | 6.64e-07 | 2.2283e-05 | 5e-06 | 2.6142e-05
4120 | 5.67e-07 | 1.33e-07 | 6.12e-07 | 2.2323e-05 | 5.2362e-06 | 2.4094e-05
4160 | 5.66e-07 | 1.37e-07 | 5.58e-07 | 2.2283e-05 | 5.3937e-06 | 2.1969e-05
4200 | 5.66e-07 | 1.4e-07 | 5.06e-07 | 2.2283e-05 | 5.5118e-06 | 1.9921e-05
4240 | 5.65e-07 | 1.41e-07 | 4.57e-07 | 2.2244e-05 | 5.5512e-06 | 1.7992e-05
4280 | 5.63e-07 | 1.42e-07 | 4.12e-07 | 2.2165e-05 | 5.5906e-06 | 1.622e-05
4320 | 5.62e-07 | 1.42e-07 | 3.7e-07 | 2.2126e-05 | 5.5906e-06 | 1.4567e-05
4360 | 5.6e-07 | 1.41e-07 | 3.3e-07 | 2.2047e-05 | 5.5512e-06 | 1.2992e-05
4400 | 5.58e-07 | 1.4e-07 | 2.94e-07 | 2.1969e-05 | 5.5118e-06 | 1.1575e-05
4440 | 5.56e-07 | 1.39e-07 | 2.61e-07 | 2.189e-05 | 5.4724e-06 | 1.0276e-05
4480 | 5.54e-07 | 1.37e-07 | 2.3e-07 | 2.1811e-05 | 5.3937e-06 | 9.0551e-06
4520 | 5.51e-07 | 1.35e-07 | 2.01e-07 | 2.1693e-05 | 5.315e-06 | 7.9134e-06
4560 | 5.49e-07 | 1.34e-07 | 1.74e-07 | 2.1614e-05 | 5.2756e-06 | 6.8504e-06
4600 | 5.47e-07 | 1.32e-07 | 1.49e-07 | 2.1535e-05 | 5.1969e-06 | 5.8661e-06
4640 | 5.45e-07 | 1.3e-07 | 1.25e-07 | 2.1457e-05 | 5.1181e-06 | 4.9213e-06
4680 | 5.42e-07 | 1.27e-07 | 1.04e-07 | 2.1339e-05 | 5e-06 | 4.0945e-06
4720 | 5.4e-07 | 1.25e-07 | 8.6e-08 | 2.126e-05 | 4.9213e-06 | 3.3858e-06
4760 | 5.37e-07 | 1.23e-07 | 7.28e-08 | 2.1142e-05 | 4.8425e-06 | 2.8661e-06
4800 | 5.35e-07 | 1.2e-07 | 6.74e-08 | 2.1063e-05 | 4.7244e-06 | 2.6535e-06
(y) max | 5.67e-07 | 1.42e-07 | 7.56e-07 | 2.2323e-05 | 5.5906e-06 | 2.9764e-05
(y') max | 0.00021375 | 5.3533e-05 | 0.00028501 | 0.0084155 | 0.0021076 | 0.011221
Not noticeable to persons
Barely noticeable to persons
Easily noticeable to persons
No faults
Minor faults
Fault
Machine Curve
2880 rpm
3600 rpm
4320 rpm
Troublesome to persons
extremely mooth
very smooth
smooth
very good
good
fair
No faults
Minor faults
Faulty
Machine Curve
good
fair
extremely smooth
Vendor Limit = 2.54 mm/s
Industry Limit

## P4_Frozen UB
Point 4: At NW Corner
Lower Bound Soil
Pump Operating = 4215 rpm
Frequency (rpm) | Amplitude (m) |  |  | Amplitude (in)
| x | y | z | x | y | z
0 | 3.24e-18 | 4.77e-19 | 4.91e-18 | 1.2756e-16 | 1.878e-17 | 1.9331e-16
40 | 7.94e-11 | 9.71e-12 | 8.84e-11 | 3.126e-09 | 3.8228e-10 | 3.4803e-09
80 | 3.22e-10 | 3.93e-11 | 3.5e-10 | 1.2677e-08 | 1.5472e-09 | 1.378e-08
120 | 7.25e-10 | 8.86e-11 | 7.79e-10 | 2.8543e-08 | 3.4882e-09 | 3.0669e-08
160 | 1.29e-09 | 1.58e-10 | 1.37e-09 | 5.0787e-08 | 6.2205e-09 | 5.3937e-08
200 | 2.03e-09 | 2.48e-10 | 2.13e-09 | 7.9921e-08 | 9.7638e-09 | 8.3858e-08
240 | 2.95e-09 | 3.6e-10 | 3.05e-09 | 1.1614e-07 | 1.4173e-08 | 1.2008e-07
280 | 4.04e-09 | 4.94e-10 | 4.13e-09 | 1.5906e-07 | 1.9449e-08 | 1.626e-07
320 | 5.33e-09 | 6.5e-10 | 5.37e-09 | 2.0984e-07 | 2.5591e-08 | 2.1142e-07
360 | 6.81e-09 | 8.3e-10 | 6.76e-09 | 2.6811e-07 | 3.2677e-08 | 2.6614e-07
400 | 8.5e-09 | 1.03e-09 | 8.32e-09 | 3.3465e-07 | 4.0551e-08 | 3.2756e-07
440 | 1.04e-08 | 1.26e-09 | 1e-08 | 4.0945e-07 | 4.9606e-08 | 3.937e-07
480 | 1.26e-08 | 1.51e-09 | 1.19e-08 | 4.9606e-07 | 5.9449e-08 | 4.685e-07
520 | 1.49e-08 | 1.78e-09 | 1.39e-08 | 5.8661e-07 | 7.0079e-08 | 5.4724e-07
560 | 1.76e-08 | 2.09e-09 | 1.61e-08 | 6.9291e-07 | 8.2283e-08 | 6.3386e-07
600 | 2.05e-08 | 2.41e-09 | 1.85e-08 | 8.0709e-07 | 9.4882e-08 | 7.2835e-07
640 | 2.36e-08 | 2.76e-09 | 2.1e-08 | 9.2913e-07 | 1.0866e-07 | 8.2677e-07
680 | 2.71e-08 | 3.14e-09 | 2.36e-08 | 1.0669e-06 | 1.2362e-07 | 9.2913e-07
720 | 3.1e-08 | 3.55e-09 | 2.65e-08 | 1.2205e-06 | 1.3976e-07 | 1.0433e-06
760 | 3.51e-08 | 3.98e-09 | 2.95e-08 | 1.3819e-06 | 1.5669e-07 | 1.1614e-06
800 | 3.97e-08 | 4.43e-09 | 3.27e-08 | 1.563e-06 | 1.7441e-07 | 1.2874e-06
840 | 4.47e-08 | 4.91e-09 | 3.62e-08 | 1.7598e-06 | 1.9331e-07 | 1.4252e-06
880 | 5.02e-08 | 5.41e-09 | 3.99e-08 | 1.9764e-06 | 2.1299e-07 | 1.5709e-06
920 | 5.61e-08 | 5.93e-09 | 4.39e-08 | 2.2087e-06 | 2.3346e-07 | 1.7283e-06
960 | 6.26e-08 | 6.48e-09 | 4.82e-08 | 2.4646e-06 | 2.5512e-07 | 1.8976e-06
1000 | 6.97e-08 | 7.03e-09 | 5.28e-08 | 2.7441e-06 | 2.7677e-07 | 2.0787e-06
1040 | 7.74e-08 | 7.61e-09 | 5.79e-08 | 3.0472e-06 | 2.9961e-07 | 2.2795e-06
1080 | 8.58e-08 | 8.19e-09 | 6.35e-08 | 3.378e-06 | 3.2244e-07 | 2.5e-06
1120 | 9.48e-08 | 8.77e-09 | 6.93e-08 | 3.7323e-06 | 3.4528e-07 | 2.7283e-06
1160 | 1.05e-07 | 9.36e-09 | 7.58e-08 | 4.1339e-06 | 3.685e-07 | 2.9843e-06
1200 | 1.15e-07 | 9.94e-09 | 8.28e-08 | 4.5276e-06 | 3.9134e-07 | 3.2598e-06
1240 | 1.27e-07 | 1.05e-08 | 9.05e-08 | 5e-06 | 4.1339e-07 | 3.563e-06
1280 | 1.4e-07 | 1.11e-08 | 9.9e-08 | 5.5118e-06 | 4.3701e-07 | 3.8976e-06
1320 | 1.53e-07 | 1.16e-08 | 1.08e-07 | 6.0236e-06 | 4.5669e-07 | 4.252e-06
1360 | 1.68e-07 | 1.2e-08 | 1.18e-07 | 6.6142e-06 | 4.7244e-07 | 4.6457e-06
1400 | 1.84e-07 | 1.25e-08 | 1.29e-07 | 7.2441e-06 | 4.9213e-07 | 5.0787e-06
1440 | 2.02e-07 | 1.29e-08 | 1.41e-07 | 7.9528e-06 | 5.0787e-07 | 5.5512e-06
1480 | 2.2e-07 | 1.32e-08 | 1.54e-07 | 8.6614e-06 | 5.1969e-07 | 6.063e-06
1520 | 2.4e-07 | 1.34e-08 | 1.68e-07 | 9.4488e-06 | 5.2756e-07 | 6.6142e-06
1560 | 2.6e-07 | 1.36e-08 | 1.83e-07 | 1.0236e-05 | 5.3543e-07 | 7.2047e-06
1600 | 2.82e-07 | 1.37e-08 | 1.98e-07 | 1.1102e-05 | 5.3937e-07 | 7.7953e-06
1640 | 3.04e-07 | 1.38e-08 | 2.14e-07 | 1.1969e-05 | 5.4331e-07 | 8.4252e-06
1680 | 3.27e-07 | 1.38e-08 | 2.3e-07 | 1.2874e-05 | 5.4331e-07 | 9.0551e-06
1720 | 3.5e-07 | 1.4e-08 | 2.46e-07 | 1.378e-05 | 5.5118e-07 | 9.685e-06
1760 | 3.72e-07 | 1.42e-08 | 2.62e-07 | 1.4646e-05 | 5.5906e-07 | 1.0315e-05
1800 | 3.92e-07 | 1.45e-08 | 2.77e-07 | 1.5433e-05 | 5.7087e-07 | 1.0906e-05
1840 | 4.11e-07 | 1.5e-08 | 2.9e-07 | 1.6181e-05 | 5.9055e-07 | 1.1417e-05
1880 | 4.29e-07 | 1.57e-08 | 3.03e-07 | 1.689e-05 | 6.1811e-07 | 1.1929e-05
1920 | 4.43e-07 | 1.66e-08 | 3.13e-07 | 1.7441e-05 | 6.5354e-07 | 1.2323e-05
1960 | 4.56e-07 | 1.77e-08 | 3.23e-07 | 1.7953e-05 | 6.9685e-07 | 1.2717e-05
2000 | 4.65e-07 | 1.89e-08 | 3.3e-07 | 1.8307e-05 | 7.4409e-07 | 1.2992e-05
2040 | 4.73e-07 | 2.02e-08 | 3.36e-07 | 1.8622e-05 | 7.9528e-07 | 1.3228e-05
2080 | 4.78e-07 | 2.15e-08 | 3.42e-07 | 1.8819e-05 | 8.4646e-07 | 1.3465e-05
2120 | 4.81e-07 | 2.29e-08 | 3.46e-07 | 1.8937e-05 | 9.0157e-07 | 1.3622e-05
2160 | 4.83e-07 | 2.42e-08 | 3.5e-07 | 1.9016e-05 | 9.5276e-07 | 1.378e-05
2200 | 4.84e-07 | 2.55e-08 | 3.54e-07 | 1.9055e-05 | 1.0039e-06 | 1.3937e-05
2240 | 4.84e-07 | 2.67e-08 | 3.58e-07 | 1.9055e-05 | 1.0512e-06 | 1.4094e-05
2280 | 4.83e-07 | 2.78e-08 | 3.62e-07 | 1.9016e-05 | 1.0945e-06 | 1.4252e-05
2320 | 4.82e-07 | 2.89e-08 | 3.67e-07 | 1.8976e-05 | 1.1378e-06 | 1.4449e-05
2360 | 4.8e-07 | 2.99e-08 | 3.73e-07 | 1.8898e-05 | 1.1772e-06 | 1.4685e-05
2400 | 4.79e-07 | 3.09e-08 | 3.79e-07 | 1.8858e-05 | 1.2165e-06 | 1.4921e-05
2440 | 4.77e-07 | 3.18e-08 | 3.86e-07 | 1.878e-05 | 1.252e-06 | 1.5197e-05
2480 | 4.76e-07 | 3.28e-08 | 3.94e-07 | 1.874e-05 | 1.2913e-06 | 1.5512e-05
2520 | 4.74e-07 | 3.38e-08 | 4.03e-07 | 1.8661e-05 | 1.3307e-06 | 1.5866e-05
2560 | 4.73e-07 | 3.49e-08 | 4.13e-07 | 1.8622e-05 | 1.374e-06 | 1.626e-05
2600 | 4.72e-07 | 3.62e-08 | 4.24e-07 | 1.8583e-05 | 1.4252e-06 | 1.6693e-05
2640 | 4.71e-07 | 3.76e-08 | 4.36e-07 | 1.8543e-05 | 1.4803e-06 | 1.7165e-05
2680 | 4.7e-07 | 3.93e-08 | 4.49e-07 | 1.8504e-05 | 1.5472e-06 | 1.7677e-05
2720 | 4.7e-07 | 4.17e-08 | 4.63e-07 | 1.8504e-05 | 1.6417e-06 | 1.8228e-05
2760 | 4.69e-07 | 4.4e-08 | 4.77e-07 | 1.8465e-05 | 1.7323e-06 | 1.878e-05
2800 | 4.69e-07 | 4.66e-08 | 4.92e-07 | 1.8465e-05 | 1.8346e-06 | 1.937e-05
2840 | 4.69e-07 | 4.95e-08 | 5.08e-07 | 1.8465e-05 | 1.9488e-06 | 2e-05
2880 | 4.69e-07 | 5.28e-08 | 5.23e-07 | 1.8465e-05 | 2.0787e-06 | 2.0591e-05
2920 | 4.69e-07 | 5.65e-08 | 5.39e-07 | 1.8465e-05 | 2.2244e-06 | 2.122e-05
2960 | 4.69e-07 | 6.05e-08 | 5.55e-07 | 1.8465e-05 | 2.3819e-06 | 2.185e-05
3000 | 4.69e-07 | 6.48e-08 | 5.71e-07 | 1.8465e-05 | 2.5512e-06 | 2.248e-05
3040 | 4.68e-07 | 6.93e-08 | 5.87e-07 | 1.8425e-05 | 2.7283e-06 | 2.311e-05
3080 | 4.67e-07 | 7.42e-08 | 6.03e-07 | 1.8386e-05 | 2.9213e-06 | 2.374e-05
3120 | 4.65e-07 | 7.92e-08 | 6.19e-07 | 1.8307e-05 | 3.1181e-06 | 2.437e-05
3160 | 4.63e-07 | 8.44e-08 | 6.35e-07 | 1.8228e-05 | 3.3228e-06 | 2.5e-05
3200 | 4.6e-07 | 8.97e-08 | 6.5e-07 | 1.811e-05 | 3.5315e-06 | 2.5591e-05
3240 | 4.56e-07 | 9.49e-08 | 6.66e-07 | 1.7953e-05 | 3.7362e-06 | 2.622e-05
3280 | 4.51e-07 | 1e-07 | 6.83e-07 | 1.7756e-05 | 3.937e-06 | 2.689e-05
3320 | 4.45e-07 | 1.05e-07 | 7.01e-07 | 1.752e-05 | 4.1339e-06 | 2.7598e-05
3360 | 4.38e-07 | 1.1e-07 | 7.2e-07 | 1.7244e-05 | 4.3307e-06 | 2.8346e-05
3400 | 4.3e-07 | 1.14e-07 | 7.41e-07 | 1.6929e-05 | 4.4882e-06 | 2.9173e-05
3440 | 4.22e-07 | 1.17e-07 | 7.66e-07 | 1.6614e-05 | 4.6063e-06 | 3.0157e-05
3480 | 4.12e-07 | 1.2e-07 | 7.94e-07 | 1.622e-05 | 4.7244e-06 | 3.126e-05
3520 | 4.01e-07 | 1.22e-07 | 8.27e-07 | 1.5787e-05 | 4.8031e-06 | 3.2559e-05
3560 | 3.9e-07 | 1.23e-07 | 8.66e-07 | 1.5354e-05 | 4.8425e-06 | 3.4094e-05
3600 | 3.78e-07 | 1.24e-07 | 9.12e-07 | 1.4882e-05 | 4.8819e-06 | 3.5906e-05
3640 | 3.66e-07 | 1.23e-07 | 9.66e-07 | 1.4409e-05 | 4.8425e-06 | 3.8031e-05
3680 | 3.54e-07 | 1.2e-07 | 1.03e-06 | 1.3937e-05 | 4.7244e-06 | 4.0551e-05
3720 | 3.42e-07 | 1.17e-07 | 1.1e-06 | 1.3465e-05 | 4.6063e-06 | 4.3307e-05
3760 | 3.29e-07 | 1.12e-07 | 1.18e-06 | 1.2953e-05 | 4.4094e-06 | 4.6457e-05
3800 | 3.17e-07 | 1.06e-07 | 1.26e-06 | 1.248e-05 | 4.1732e-06 | 4.9606e-05
3840 | 3.04e-07 | 1.01e-07 | 1.33e-06 | 1.1969e-05 | 3.9764e-06 | 5.2362e-05
3880 | 2.9e-07 | 9.69e-08 | 1.39e-06 | 1.1417e-05 | 3.815e-06 | 5.4724e-05
3920 | 2.76e-07 | 9.71e-08 | 1.42e-06 | 1.0866e-05 | 3.8228e-06 | 5.5906e-05
3960 | 2.61e-07 | 1.02e-07 | 1.4e-06 | 1.0276e-05 | 4.0157e-06 | 5.5118e-05
4000 | 2.47e-07 | 1.1e-07 | 1.34e-06 | 9.7244e-06 | 4.3307e-06 | 5.2756e-05
4040 | 2.33e-07 | 1.19e-07 | 1.24e-06 | 9.1732e-06 | 4.685e-06 | 4.8819e-05
4080 | 2.2e-07 | 1.27e-07 | 1.13e-06 | 8.6614e-06 | 5e-06 | 4.4488e-05
4120 | 2.1e-07 | 1.33e-07 | 1.01e-06 | 8.2677e-06 | 5.2362e-06 | 3.9764e-05
4160 | 2e-07 | 1.37e-07 | 8.99e-07 | 7.874e-06 | 5.3937e-06 | 3.5394e-05
4200 | 1.92e-07 | 1.4e-07 | 7.95e-07 | 7.5591e-06 | 5.5118e-06 | 3.1299e-05
4240 | 1.86e-07 | 1.41e-07 | 7.04e-07 | 7.3228e-06 | 5.5512e-06 | 2.7717e-05
4280 | 1.8e-07 | 1.42e-07 | 6.25e-07 | 7.0866e-06 | 5.5906e-06 | 2.4606e-05
4320 | 1.74e-07 | 1.42e-07 | 5.56e-07 | 6.8504e-06 | 5.5906e-06 | 2.189e-05
4360 | 1.7e-07 | 1.41e-07 | 5e-07 | 6.6929e-06 | 5.5512e-06 | 1.9685e-05
4400 | 1.66e-07 | 1.4e-07 | 4.55e-07 | 6.5354e-06 | 5.5118e-06 | 1.7913e-05
4440 | 1.63e-07 | 1.39e-07 | 4.21e-07 | 6.4173e-06 | 5.4724e-06 | 1.6575e-05
4480 | 1.61e-07 | 1.37e-07 | 3.99e-07 | 6.3386e-06 | 5.3937e-06 | 1.5709e-05
4520 | 1.59e-07 | 1.35e-07 | 3.87e-07 | 6.2598e-06 | 5.315e-06 | 1.5236e-05
4560 | 1.58e-07 | 1.34e-07 | 3.86e-07 | 6.2205e-06 | 5.2756e-06 | 1.5197e-05
4600 | 1.56e-07 | 1.32e-07 | 3.94e-07 | 6.1417e-06 | 5.1969e-06 | 1.5512e-05
4640 | 1.56e-07 | 1.3e-07 | 4.09e-07 | 6.1417e-06 | 5.1181e-06 | 1.6102e-05
4680 | 1.55e-07 | 1.27e-07 | 4.3e-07 | 6.1024e-06 | 5e-06 | 1.6929e-05
4720 | 1.55e-07 | 1.25e-07 | 4.56e-07 | 6.1024e-06 | 4.9213e-06 | 1.7953e-05
4760 | 1.55e-07 | 1.23e-07 | 4.85e-07 | 6.1024e-06 | 4.8425e-06 | 1.9094e-05
4800 | 1.55e-07 | 1.2e-07 | 5.16e-07 | 6.1024e-06 | 4.7244e-06 | 2.0315e-05
(y) max | 4.84e-07 | 1.42e-07 | 1.42e-06 | 1.9055e-05 | 5.5906e-06 | 5.5906e-05
(y') max | 0.00018246 | 5.3533e-05 | 0.00053533 | 0.0071836 | 0.0021076 | 0.021076
Not noticeable to persons
Barely noticeable to persons
Easily noticeable to persons
No faults
Minor faults
Fault
Machine Curve
2880 rpm
3600 rpm
4320 rpm
Troublesome to persons
extremely mooth
very smooth
smooth
very good
good
fair
No faults
Minor faults
Faulty
Machine Curve
good
fair
extremely smooth
Vendor Limit = 2.54 mm/s
Industry Limit

## P5_Frozen UB
Point 5: At NE Corner
Lower Bound Soil
Pump Operating = 4215 rpm
Frequency (rpm) | Amplitude (m) |  |  | Amplitude (in)
| x | y | z | x | y | z
0 | 3.24e-18 | 4.65e-19 | 4.79e-18 | 1.2756e-16 | 1.8307e-17 | 1.8858e-16
40 | 7.94e-11 | 9.73e-12 | 8.81e-11 | 3.126e-09 | 3.8307e-10 | 3.4685e-09
80 | 3.22e-10 | 3.95e-11 | 3.56e-10 | 1.2677e-08 | 1.5551e-09 | 1.4016e-08
120 | 7.25e-10 | 8.92e-11 | 8.09e-10 | 2.8543e-08 | 3.5118e-09 | 3.185e-08
160 | 1.29e-09 | 1.6e-10 | 1.45e-09 | 5.0787e-08 | 6.2992e-09 | 5.7087e-08
200 | 2.03e-09 | 2.52e-10 | 2.29e-09 | 7.9921e-08 | 9.9213e-09 | 9.0157e-08
240 | 2.95e-09 | 3.67e-10 | 3.33e-09 | 1.1614e-07 | 1.4449e-08 | 1.311e-07
280 | 4.04e-09 | 5.05e-10 | 4.59e-09 | 1.5906e-07 | 1.9882e-08 | 1.8071e-07
320 | 5.33e-09 | 6.69e-10 | 6.06e-09 | 2.0984e-07 | 2.6339e-08 | 2.3858e-07
360 | 6.81e-09 | 8.59e-10 | 7.76e-09 | 2.6811e-07 | 3.3819e-08 | 3.0551e-07
400 | 8.5e-09 | 1.08e-09 | 9.69e-09 | 3.3465e-07 | 4.252e-08 | 3.815e-07
440 | 1.04e-08 | 1.33e-09 | 1.19e-08 | 4.0945e-07 | 5.2362e-08 | 4.685e-07
480 | 1.26e-08 | 1.61e-09 | 1.43e-08 | 4.9606e-07 | 6.3386e-08 | 5.6299e-07
520 | 1.49e-08 | 1.93e-09 | 1.7e-08 | 5.8661e-07 | 7.5984e-08 | 6.6929e-07
560 | 1.76e-08 | 2.28e-09 | 2e-08 | 6.9291e-07 | 8.9764e-08 | 7.874e-07
600 | 2.05e-08 | 2.67e-09 | 2.32e-08 | 8.0709e-07 | 1.0512e-07 | 9.1339e-07
640 | 2.36e-08 | 3.1e-09 | 2.67e-08 | 9.2913e-07 | 1.2205e-07 | 1.0512e-06
680 | 2.71e-08 | 3.57e-09 | 3.05e-08 | 1.0669e-06 | 1.4055e-07 | 1.2008e-06
720 | 3.1e-08 | 4.1e-09 | 3.46e-08 | 1.2205e-06 | 1.6142e-07 | 1.3622e-06
760 | 3.51e-08 | 4.67e-09 | 3.89e-08 | 1.3819e-06 | 1.8386e-07 | 1.5315e-06
800 | 3.97e-08 | 5.29e-09 | 4.35e-08 | 1.563e-06 | 2.0827e-07 | 1.7126e-06
840 | 4.47e-08 | 5.97e-09 | 4.84e-08 | 1.7598e-06 | 2.3504e-07 | 1.9055e-06
880 | 5.02e-08 | 6.72e-09 | 5.35e-08 | 1.9764e-06 | 2.6457e-07 | 2.1063e-06
920 | 5.61e-08 | 7.52e-09 | 5.9e-08 | 2.2087e-06 | 2.9606e-07 | 2.3228e-06
960 | 6.26e-08 | 8.4e-09 | 6.46e-08 | 2.4646e-06 | 3.3071e-07 | 2.5433e-06
1000 | 6.97e-08 | 9.35e-09 | 7.05e-08 | 2.7441e-06 | 3.6811e-07 | 2.7756e-06
1040 | 7.74e-08 | 1.04e-08 | 7.67e-08 | 3.0472e-06 | 4.0945e-07 | 3.0197e-06
1080 | 8.58e-08 | 1.15e-08 | 8.32e-08 | 3.378e-06 | 4.5276e-07 | 3.2756e-06
1120 | 9.48e-08 | 1.26e-08 | 8.96e-08 | 3.7323e-06 | 4.9606e-07 | 3.5276e-06
1160 | 1.05e-07 | 1.38e-08 | 9.63e-08 | 4.1339e-06 | 5.4331e-07 | 3.7913e-06
1200 | 1.15e-07 | 1.51e-08 | 1.03e-07 | 4.5276e-06 | 5.9449e-07 | 4.0551e-06
1240 | 1.27e-07 | 1.65e-08 | 1.1e-07 | 5e-06 | 6.4961e-07 | 4.3307e-06
1280 | 1.4e-07 | 1.8e-08 | 1.18e-07 | 5.5118e-06 | 7.0866e-07 | 4.6457e-06
1320 | 1.53e-07 | 1.95e-08 | 1.25e-07 | 6.0236e-06 | 7.6772e-07 | 4.9213e-06
1360 | 1.68e-07 | 2.11e-08 | 1.33e-07 | 6.6142e-06 | 8.3071e-07 | 5.2362e-06
1400 | 1.84e-07 | 2.28e-08 | 1.4e-07 | 7.2441e-06 | 8.9764e-07 | 5.5118e-06
1440 | 2.02e-07 | 2.45e-08 | 1.48e-07 | 7.9528e-06 | 9.6457e-07 | 5.8268e-06
1480 | 2.2e-07 | 2.63e-08 | 1.56e-07 | 8.6614e-06 | 1.0354e-06 | 6.1417e-06
1520 | 2.4e-07 | 2.81e-08 | 1.63e-07 | 9.4488e-06 | 1.1063e-06 | 6.4173e-06
1560 | 2.6e-07 | 3e-08 | 1.71e-07 | 1.0236e-05 | 1.1811e-06 | 6.7323e-06
1600 | 2.82e-07 | 3.18e-08 | 1.78e-07 | 1.1102e-05 | 1.252e-06 | 7.0079e-06
1640 | 3.04e-07 | 3.37e-08 | 1.84e-07 | 1.1969e-05 | 1.3268e-06 | 7.2441e-06
1680 | 3.27e-07 | 3.56e-08 | 1.9e-07 | 1.2874e-05 | 1.4016e-06 | 7.4803e-06
1720 | 3.5e-07 | 3.75e-08 | 1.95e-07 | 1.378e-05 | 1.4764e-06 | 7.6772e-06
1760 | 3.72e-07 | 3.94e-08 | 1.99e-07 | 1.4646e-05 | 1.5512e-06 | 7.8346e-06
1800 | 3.92e-07 | 4.14e-08 | 2.02e-07 | 1.5433e-05 | 1.6299e-06 | 7.9528e-06
1840 | 4.11e-07 | 4.34e-08 | 2.04e-07 | 1.6181e-05 | 1.7087e-06 | 8.0315e-06
1880 | 4.29e-07 | 4.54e-08 | 2.04e-07 | 1.689e-05 | 1.7874e-06 | 8.0315e-06
1920 | 4.43e-07 | 4.76e-08 | 2.02e-07 | 1.7441e-05 | 1.874e-06 | 7.9528e-06
1960 | 4.56e-07 | 4.98e-08 | 1.99e-07 | 1.7953e-05 | 1.9606e-06 | 7.8346e-06
2000 | 4.65e-07 | 5.22e-08 | 1.95e-07 | 1.8307e-05 | 2.0551e-06 | 7.6772e-06
2040 | 4.73e-07 | 5.48e-08 | 1.89e-07 | 1.8622e-05 | 2.1575e-06 | 7.4409e-06
2080 | 4.78e-07 | 5.75e-08 | 1.83e-07 | 1.8819e-05 | 2.2638e-06 | 7.2047e-06
2120 | 4.81e-07 | 6.05e-08 | 1.75e-07 | 1.8937e-05 | 2.3819e-06 | 6.8898e-06
2160 | 4.83e-07 | 6.36e-08 | 1.66e-07 | 1.9016e-05 | 2.5039e-06 | 6.5354e-06
2200 | 4.84e-07 | 6.71e-08 | 1.57e-07 | 1.9055e-05 | 2.6417e-06 | 6.1811e-06
2240 | 4.84e-07 | 7.08e-08 | 1.47e-07 | 1.9055e-05 | 2.7874e-06 | 5.7874e-06
2280 | 4.83e-07 | 7.47e-08 | 1.36e-07 | 1.9016e-05 | 2.9409e-06 | 5.3543e-06
2320 | 4.82e-07 | 7.89e-08 | 1.24e-07 | 1.8976e-05 | 3.1063e-06 | 4.8819e-06
2360 | 4.8e-07 | 8.34e-08 | 1.12e-07 | 1.8898e-05 | 3.2835e-06 | 4.4094e-06
2400 | 4.79e-07 | 8.81e-08 | 9.96e-08 | 1.8858e-05 | 3.4685e-06 | 3.9213e-06
2440 | 4.77e-07 | 9.3e-08 | 8.65e-08 | 1.878e-05 | 3.6614e-06 | 3.4055e-06
2480 | 4.76e-07 | 9.83e-08 | 7.3e-08 | 1.874e-05 | 3.8701e-06 | 2.874e-06
2520 | 4.74e-07 | 1.04e-07 | 5.92e-08 | 1.8661e-05 | 4.0945e-06 | 2.3307e-06
2560 | 4.73e-07 | 1.09e-07 | 4.55e-08 | 1.8622e-05 | 4.2913e-06 | 1.7913e-06
2600 | 4.72e-07 | 1.15e-07 | 3.29e-08 | 1.8583e-05 | 4.5276e-06 | 1.2953e-06
2640 | 4.71e-07 | 1.21e-07 | 2.44e-08 | 1.8543e-05 | 4.7638e-06 | 9.6063e-07
2680 | 4.7e-07 | 1.27e-07 | 2.59e-08 | 1.8504e-05 | 5e-06 | 1.0197e-06
2720 | 4.7e-07 | 1.34e-07 | 3.65e-08 | 1.8504e-05 | 5.2756e-06 | 1.437e-06
2760 | 4.69e-07 | 1.41e-07 | 5.13e-08 | 1.8465e-05 | 5.5512e-06 | 2.0197e-06
2800 | 4.69e-07 | 1.47e-07 | 6.78e-08 | 1.8465e-05 | 5.7874e-06 | 2.6693e-06
2840 | 4.69e-07 | 1.54e-07 | 8.52e-08 | 1.8465e-05 | 6.063e-06 | 3.3543e-06
2880 | 4.69e-07 | 1.61e-07 | 1.03e-07 | 1.8465e-05 | 6.3386e-06 | 4.0551e-06
2920 | 4.69e-07 | 1.68e-07 | 1.21e-07 | 1.8465e-05 | 6.6142e-06 | 4.7638e-06
2960 | 4.69e-07 | 1.74e-07 | 1.4e-07 | 1.8465e-05 | 6.8504e-06 | 5.5118e-06
3000 | 4.69e-07 | 1.81e-07 | 1.58e-07 | 1.8465e-05 | 7.126e-06 | 6.2205e-06
3040 | 4.68e-07 | 1.88e-07 | 1.76e-07 | 1.8425e-05 | 7.4016e-06 | 6.9291e-06
3080 | 4.67e-07 | 1.95e-07 | 1.94e-07 | 1.8386e-05 | 7.6772e-06 | 7.6378e-06
3120 | 4.65e-07 | 2.01e-07 | 2.11e-07 | 1.8307e-05 | 7.9134e-06 | 8.3071e-06
3160 | 4.63e-07 | 2.07e-07 | 2.28e-07 | 1.8228e-05 | 8.1496e-06 | 8.9764e-06
3200 | 4.6e-07 | 2.14e-07 | 2.45e-07 | 1.811e-05 | 8.4252e-06 | 9.6457e-06
3240 | 4.56e-07 | 2.19e-07 | 2.62e-07 | 1.7953e-05 | 8.622e-06 | 1.0315e-05
3280 | 4.51e-07 | 2.25e-07 | 2.78e-07 | 1.7756e-05 | 8.8583e-06 | 1.0945e-05
3320 | 4.45e-07 | 2.3e-07 | 2.96e-07 | 1.752e-05 | 9.0551e-06 | 1.1654e-05
3360 | 4.38e-07 | 2.34e-07 | 3.14e-07 | 1.7244e-05 | 9.2126e-06 | 1.2362e-05
3400 | 4.3e-07 | 2.38e-07 | 3.34e-07 | 1.6929e-05 | 9.3701e-06 | 1.315e-05
3440 | 4.22e-07 | 2.42e-07 | 3.56e-07 | 1.6614e-05 | 9.5276e-06 | 1.4016e-05
3480 | 4.12e-07 | 2.45e-07 | 3.83e-07 | 1.622e-05 | 9.6457e-06 | 1.5079e-05
3520 | 4.01e-07 | 2.48e-07 | 4.14e-07 | 1.5787e-05 | 9.7638e-06 | 1.6299e-05
3560 | 3.9e-07 | 2.51e-07 | 4.53e-07 | 1.5354e-05 | 9.8819e-06 | 1.7835e-05
3600 | 3.78e-07 | 2.54e-07 | 5e-07 | 1.4882e-05 | 1e-05 | 1.9685e-05
3640 | 3.66e-07 | 2.56e-07 | 5.57e-07 | 1.4409e-05 | 1.0079e-05 | 2.1929e-05
3680 | 3.54e-07 | 2.59e-07 | 6.26e-07 | 1.3937e-05 | 1.0197e-05 | 2.4646e-05
3720 | 3.42e-07 | 2.63e-07 | 7.1e-07 | 1.3465e-05 | 1.0354e-05 | 2.7953e-05
3760 | 3.29e-07 | 2.66e-07 | 8.07e-07 | 1.2953e-05 | 1.0472e-05 | 3.1772e-05
3800 | 3.17e-07 | 2.69e-07 | 9.18e-07 | 1.248e-05 | 1.0591e-05 | 3.6142e-05
3840 | 3.04e-07 | 2.72e-07 | 1.04e-06 | 1.1969e-05 | 1.0709e-05 | 4.0945e-05
3880 | 2.9e-07 | 2.72e-07 | 1.15e-06 | 1.1417e-05 | 1.0709e-05 | 4.5276e-05
3920 | 2.76e-07 | 2.69e-07 | 1.25e-06 | 1.0866e-05 | 1.0591e-05 | 4.9213e-05
3960 | 2.61e-07 | 2.63e-07 | 1.32e-06 | 1.0276e-05 | 1.0354e-05 | 5.1969e-05
4000 | 2.47e-07 | 2.53e-07 | 1.35e-06 | 9.7244e-06 | 9.9606e-06 | 5.315e-05
4040 | 2.33e-07 | 2.4e-07 | 1.34e-06 | 9.1732e-06 | 9.4488e-06 | 5.2756e-05
4080 | 2.2e-07 | 2.28e-07 | 1.3e-06 | 8.6614e-06 | 8.9764e-06 | 5.1181e-05
4120 | 2.1e-07 | 2.16e-07 | 1.25e-06 | 8.2677e-06 | 8.5039e-06 | 4.9213e-05
4160 | 2e-07 | 2.06e-07 | 1.19e-06 | 7.874e-06 | 8.1102e-06 | 4.685e-05
4200 | 1.92e-07 | 1.97e-07 | 1.13e-06 | 7.5591e-06 | 7.7559e-06 | 4.4488e-05
4240 | 1.86e-07 | 1.9e-07 | 1.07e-06 | 7.3228e-06 | 7.4803e-06 | 4.2126e-05
4280 | 1.8e-07 | 1.84e-07 | 1.02e-06 | 7.0866e-06 | 7.2441e-06 | 4.0157e-05
4320 | 1.74e-07 | 1.8e-07 | 9.8e-07 | 6.8504e-06 | 7.0866e-06 | 3.8583e-05
4360 | 1.7e-07 | 1.76e-07 | 9.41e-07 | 6.6929e-06 | 6.9291e-06 | 3.7047e-05
4400 | 1.66e-07 | 1.73e-07 | 9.07e-07 | 6.5354e-06 | 6.811e-06 | 3.5709e-05
4440 | 1.63e-07 | 1.71e-07 | 8.8e-07 | 6.4173e-06 | 6.7323e-06 | 3.4646e-05
4480 | 1.61e-07 | 1.69e-07 | 8.58e-07 | 6.3386e-06 | 6.6535e-06 | 3.378e-05
4520 | 1.59e-07 | 1.67e-07 | 8.4e-07 | 6.2598e-06 | 6.5748e-06 | 3.3071e-05
4560 | 1.58e-07 | 1.67e-07 | 8.27e-07 | 6.2205e-06 | 6.5748e-06 | 3.2559e-05
4600 | 1.56e-07 | 1.66e-07 | 8.18e-07 | 6.1417e-06 | 6.5354e-06 | 3.2205e-05
4640 | 1.56e-07 | 1.66e-07 | 8.13e-07 | 6.1417e-06 | 6.5354e-06 | 3.2008e-05
4680 | 1.55e-07 | 1.66e-07 | 8.12e-07 | 6.1024e-06 | 6.5354e-06 | 3.1969e-05
4720 | 1.55e-07 | 1.66e-07 | 8.15e-07 | 6.1024e-06 | 6.5354e-06 | 3.2087e-05
4760 | 1.55e-07 | 1.67e-07 | 8.21e-07 | 6.1024e-06 | 6.5748e-06 | 3.2323e-05
4800 | 1.55e-07 | 1.68e-07 | 8.31e-07 | 6.1024e-06 | 6.6142e-06 | 3.2717e-05
(y) max | 4.84e-07 | 2.72e-07 | 1.35e-06 | 1.9055e-05 | 1.0709e-05 | 5.315e-05
(y') max | 0.00018246 | 0.00010254 | 0.00050894 | 0.0071836 | 0.0040371 | 0.020037
Not noticeable to persons
Barely noticeable to persons
Easily noticeable to persons
No faults
Minor faults
Fault
Machine Curve
2880 rpm
3600 rpm
4320 rpm
Troublesome to persons
extremely mooth
very smooth
smooth
very good
good
fair
No faults
Minor faults
Faulty
Machine Curve
good
fair
extremely smooth
Vendor Limit = 2.54 mm/s
Industry Limit

## P6_Frozen UB
Point 6: At SE Corner
Lower Bound Soil
Pump Operating = 4215 rpm
Frequency (rpm) | Amplitude (m) |  |  | Amplitude (in)
| x | y | z | x | y | z
0 | 4.75e-18 | 4.65e-19 | 3.25e-18 | 1.8701e-16 | 1.8307e-17 | 1.2795e-16
40 | 1.06e-10 | 9.73e-12 | 6.42e-11 | 4.1732e-09 | 3.8307e-10 | 2.5276e-09
80 | 4.32e-10 | 3.95e-11 | 2.62e-10 | 1.7008e-08 | 1.5551e-09 | 1.0315e-08
120 | 9.74e-10 | 8.92e-11 | 6e-10 | 3.8346e-08 | 3.5118e-09 | 2.3622e-08
160 | 1.74e-09 | 1.6e-10 | 1.09e-09 | 6.8504e-08 | 6.2992e-09 | 4.2913e-08
200 | 2.72e-09 | 2.52e-10 | 1.73e-09 | 1.0709e-07 | 9.9213e-09 | 6.811e-08
240 | 3.95e-09 | 3.67e-10 | 2.54e-09 | 1.5551e-07 | 1.4449e-08 | 1e-07
280 | 5.41e-09 | 5.05e-10 | 3.51e-09 | 2.1299e-07 | 1.9882e-08 | 1.3819e-07
320 | 7.12e-09 | 6.69e-10 | 4.67e-09 | 2.8031e-07 | 2.6339e-08 | 1.8386e-07
360 | 9.09e-09 | 8.59e-10 | 6.02e-09 | 3.5787e-07 | 3.3819e-08 | 2.3701e-07
400 | 1.13e-08 | 1.08e-09 | 7.57e-09 | 4.4488e-07 | 4.252e-08 | 2.9803e-07
440 | 1.38e-08 | 1.33e-09 | 9.33e-09 | 5.4331e-07 | 5.2362e-08 | 3.6732e-07
480 | 1.67e-08 | 1.61e-09 | 1.13e-08 | 6.5748e-07 | 6.3386e-08 | 4.4488e-07
520 | 1.98e-08 | 1.93e-09 | 1.36e-08 | 7.7953e-07 | 7.5984e-08 | 5.3543e-07
560 | 2.32e-08 | 2.28e-09 | 1.6e-08 | 9.1339e-07 | 8.9764e-08 | 6.2992e-07
600 | 2.7e-08 | 2.67e-09 | 1.87e-08 | 1.063e-06 | 1.0512e-07 | 7.3622e-07
640 | 3.11e-08 | 3.1e-09 | 2.17e-08 | 1.2244e-06 | 1.2205e-07 | 8.5433e-07
680 | 3.56e-08 | 3.57e-09 | 2.49e-08 | 1.4016e-06 | 1.4055e-07 | 9.8031e-07
720 | 4.05e-08 | 4.1e-09 | 2.84e-08 | 1.5945e-06 | 1.6142e-07 | 1.1181e-06
760 | 4.58e-08 | 4.67e-09 | 3.21e-08 | 1.8031e-06 | 1.8386e-07 | 1.2638e-06
800 | 5.16e-08 | 5.29e-09 | 3.62e-08 | 2.0315e-06 | 2.0827e-07 | 1.4252e-06
840 | 5.78e-08 | 5.97e-09 | 4.04e-08 | 2.2756e-06 | 2.3504e-07 | 1.5906e-06
880 | 6.46e-08 | 6.72e-09 | 4.5e-08 | 2.5433e-06 | 2.6457e-07 | 1.7717e-06
920 | 7.2e-08 | 7.52e-09 | 4.98e-08 | 2.8346e-06 | 2.9606e-07 | 1.9606e-06
960 | 7.99e-08 | 8.4e-09 | 5.49e-08 | 3.1457e-06 | 3.3071e-07 | 2.1614e-06
1000 | 8.85e-08 | 9.35e-09 | 6.03e-08 | 3.4843e-06 | 3.6811e-07 | 2.374e-06
1040 | 9.78e-08 | 1.04e-08 | 6.6e-08 | 3.8504e-06 | 4.0945e-07 | 2.5984e-06
1080 | 1.08e-07 | 1.15e-08 | 7.19e-08 | 4.252e-06 | 4.5276e-07 | 2.8307e-06
1120 | 1.19e-07 | 1.26e-08 | 7.81e-08 | 4.685e-06 | 4.9606e-07 | 3.0748e-06
1160 | 1.3e-07 | 1.38e-08 | 8.45e-08 | 5.1181e-06 | 5.4331e-07 | 3.3268e-06
1200 | 1.43e-07 | 1.51e-08 | 9.13e-08 | 5.6299e-06 | 5.9449e-07 | 3.5945e-06
1240 | 1.56e-07 | 1.65e-08 | 9.85e-08 | 6.1417e-06 | 6.4961e-07 | 3.878e-06
1280 | 1.7e-07 | 1.8e-08 | 1.06e-07 | 6.6929e-06 | 7.0866e-07 | 4.1732e-06
1320 | 1.86e-07 | 1.95e-08 | 1.14e-07 | 7.3228e-06 | 7.6772e-07 | 4.4882e-06
1360 | 2.02e-07 | 2.11e-08 | 1.22e-07 | 7.9528e-06 | 8.3071e-07 | 4.8031e-06
1400 | 2.2e-07 | 2.28e-08 | 1.31e-07 | 8.6614e-06 | 8.9764e-07 | 5.1575e-06
1440 | 2.39e-07 | 2.45e-08 | 1.4e-07 | 9.4094e-06 | 9.6457e-07 | 5.5118e-06
1480 | 2.58e-07 | 2.63e-08 | 1.5e-07 | 1.0157e-05 | 1.0354e-06 | 5.9055e-06
1520 | 2.79e-07 | 2.81e-08 | 1.59e-07 | 1.0984e-05 | 1.1063e-06 | 6.2598e-06
1560 | 3e-07 | 3e-08 | 1.7e-07 | 1.1811e-05 | 1.1811e-06 | 6.6929e-06
1600 | 3.22e-07 | 3.18e-08 | 1.8e-07 | 1.2677e-05 | 1.252e-06 | 7.0866e-06
1640 | 3.44e-07 | 3.37e-08 | 1.9e-07 | 1.3543e-05 | 1.3268e-06 | 7.4803e-06
1680 | 3.66e-07 | 3.56e-08 | 2.01e-07 | 1.4409e-05 | 1.4016e-06 | 7.9134e-06
1720 | 3.87e-07 | 3.75e-08 | 2.1e-07 | 1.5236e-05 | 1.4764e-06 | 8.2677e-06
1760 | 4.06e-07 | 3.94e-08 | 2.2e-07 | 1.5984e-05 | 1.5512e-06 | 8.6614e-06
1800 | 4.24e-07 | 4.14e-08 | 2.28e-07 | 1.6693e-05 | 1.6299e-06 | 8.9764e-06
1840 | 4.39e-07 | 4.34e-08 | 2.35e-07 | 1.7283e-05 | 1.7087e-06 | 9.252e-06
1880 | 4.52e-07 | 4.54e-08 | 2.41e-07 | 1.7795e-05 | 1.7874e-06 | 9.4882e-06
1920 | 4.61e-07 | 4.76e-08 | 2.46e-07 | 1.815e-05 | 1.874e-06 | 9.685e-06
1960 | 4.68e-07 | 4.98e-08 | 2.48e-07 | 1.8425e-05 | 1.9606e-06 | 9.7638e-06
2000 | 4.71e-07 | 5.22e-08 | 2.5e-07 | 1.8543e-05 | 2.0551e-06 | 9.8425e-06
2040 | 4.72e-07 | 5.48e-08 | 2.5e-07 | 1.8583e-05 | 2.1575e-06 | 9.8425e-06
2080 | 4.7e-07 | 5.75e-08 | 2.48e-07 | 1.8504e-05 | 2.2638e-06 | 9.7638e-06
2120 | 4.66e-07 | 6.05e-08 | 2.46e-07 | 1.8346e-05 | 2.3819e-06 | 9.685e-06
2160 | 4.6e-07 | 6.36e-08 | 2.43e-07 | 1.811e-05 | 2.5039e-06 | 9.5669e-06
2200 | 4.54e-07 | 6.71e-08 | 2.4e-07 | 1.7874e-05 | 2.6417e-06 | 9.4488e-06
2240 | 4.46e-07 | 7.08e-08 | 2.36e-07 | 1.7559e-05 | 2.7874e-06 | 9.2913e-06
2280 | 4.38e-07 | 7.47e-08 | 2.33e-07 | 1.7244e-05 | 2.9409e-06 | 9.1732e-06
2320 | 4.3e-07 | 7.89e-08 | 2.29e-07 | 1.6929e-05 | 3.1063e-06 | 9.0157e-06
2360 | 4.21e-07 | 8.34e-08 | 2.25e-07 | 1.6575e-05 | 3.2835e-06 | 8.8583e-06
2400 | 4.13e-07 | 8.81e-08 | 2.22e-07 | 1.626e-05 | 3.4685e-06 | 8.7402e-06
2440 | 4.05e-07 | 9.3e-08 | 2.19e-07 | 1.5945e-05 | 3.6614e-06 | 8.622e-06
2480 | 3.97e-07 | 9.83e-08 | 2.16e-07 | 1.563e-05 | 3.8701e-06 | 8.5039e-06
2520 | 3.89e-07 | 1.04e-07 | 2.14e-07 | 1.5315e-05 | 4.0945e-06 | 8.4252e-06
2560 | 3.82e-07 | 1.09e-07 | 2.12e-07 | 1.5039e-05 | 4.2913e-06 | 8.3465e-06
2600 | 3.76e-07 | 1.15e-07 | 2.11e-07 | 1.4803e-05 | 4.5276e-06 | 8.3071e-06
2640 | 3.71e-07 | 1.21e-07 | 2.1e-07 | 1.4606e-05 | 4.7638e-06 | 8.2677e-06
2680 | 3.66e-07 | 1.27e-07 | 2.1e-07 | 1.4409e-05 | 5e-06 | 8.2677e-06
2720 | 3.62e-07 | 1.34e-07 | 2.11e-07 | 1.4252e-05 | 5.2756e-06 | 8.3071e-06
2760 | 3.59e-07 | 1.41e-07 | 2.12e-07 | 1.4134e-05 | 5.5512e-06 | 8.3465e-06
2800 | 3.58e-07 | 1.47e-07 | 2.12e-07 | 1.4094e-05 | 5.7874e-06 | 8.3465e-06
2840 | 3.57e-07 | 1.54e-07 | 2.13e-07 | 1.4055e-05 | 6.063e-06 | 8.3858e-06
2880 | 3.58e-07 | 1.61e-07 | 2.14e-07 | 1.4094e-05 | 6.3386e-06 | 8.4252e-06
2920 | 3.6e-07 | 1.68e-07 | 2.14e-07 | 1.4173e-05 | 6.6142e-06 | 8.4252e-06
2960 | 3.64e-07 | 1.74e-07 | 2.15e-07 | 1.4331e-05 | 6.8504e-06 | 8.4646e-06
3000 | 3.69e-07 | 1.81e-07 | 2.15e-07 | 1.4528e-05 | 7.126e-06 | 8.4646e-06
3040 | 3.76e-07 | 1.88e-07 | 2.15e-07 | 1.4803e-05 | 7.4016e-06 | 8.4646e-06
3080 | 3.84e-07 | 1.95e-07 | 2.14e-07 | 1.5118e-05 | 7.6772e-06 | 8.4252e-06
3120 | 3.93e-07 | 2.01e-07 | 2.13e-07 | 1.5472e-05 | 7.9134e-06 | 8.3858e-06
3160 | 4.04e-07 | 2.07e-07 | 2.12e-07 | 1.5906e-05 | 8.1496e-06 | 8.3465e-06
3200 | 4.15e-07 | 2.14e-07 | 2.1e-07 | 1.6339e-05 | 8.4252e-06 | 8.2677e-06
3240 | 4.28e-07 | 2.19e-07 | 2.07e-07 | 1.685e-05 | 8.622e-06 | 8.1496e-06
3280 | 4.41e-07 | 2.25e-07 | 2.04e-07 | 1.7362e-05 | 8.8583e-06 | 8.0315e-06
3320 | 4.54e-07 | 2.3e-07 | 1.99e-07 | 1.7874e-05 | 9.0551e-06 | 7.8346e-06
3360 | 4.67e-07 | 2.34e-07 | 1.94e-07 | 1.8386e-05 | 9.2126e-06 | 7.6378e-06
3400 | 4.81e-07 | 2.38e-07 | 1.88e-07 | 1.8937e-05 | 9.3701e-06 | 7.4016e-06
3440 | 4.93e-07 | 2.42e-07 | 1.8e-07 | 1.9409e-05 | 9.5276e-06 | 7.0866e-06
3480 | 5.05e-07 | 2.45e-07 | 1.7e-07 | 1.9882e-05 | 9.6457e-06 | 6.6929e-06
3520 | 5.16e-07 | 2.48e-07 | 1.58e-07 | 2.0315e-05 | 9.7638e-06 | 6.2205e-06
3560 | 5.26e-07 | 2.51e-07 | 1.44e-07 | 2.0709e-05 | 9.8819e-06 | 5.6693e-06
3600 | 5.34e-07 | 2.54e-07 | 1.25e-07 | 2.1024e-05 | 1e-05 | 4.9213e-06
3640 | 5.41e-07 | 2.56e-07 | 1.03e-07 | 2.1299e-05 | 1.0079e-05 | 4.0551e-06
3680 | 5.47e-07 | 2.59e-07 | 7.57e-08 | 2.1535e-05 | 1.0197e-05 | 2.9803e-06
3720 | 5.51e-07 | 2.63e-07 | 4.94e-08 | 2.1693e-05 | 1.0354e-05 | 1.9449e-06
3760 | 5.55e-07 | 2.66e-07 | 5.36e-08 | 2.185e-05 | 1.0472e-05 | 2.1102e-06
3800 | 5.57e-07 | 2.69e-07 | 1.03e-07 | 2.1929e-05 | 1.0591e-05 | 4.0551e-06
3840 | 5.58e-07 | 2.72e-07 | 1.75e-07 | 2.1969e-05 | 1.0709e-05 | 6.8898e-06
3880 | 5.59e-07 | 2.72e-07 | 2.62e-07 | 2.2008e-05 | 1.0709e-05 | 1.0315e-05
3920 | 5.6e-07 | 2.69e-07 | 3.57e-07 | 2.2047e-05 | 1.0591e-05 | 1.4055e-05
3960 | 5.62e-07 | 2.63e-07 | 4.51e-07 | 2.2126e-05 | 1.0354e-05 | 1.7756e-05
4000 | 5.63e-07 | 2.53e-07 | 5.36e-07 | 2.2165e-05 | 9.9606e-06 | 2.1102e-05
4040 | 5.65e-07 | 2.4e-07 | 6.04e-07 | 2.2244e-05 | 9.4488e-06 | 2.378e-05
4080 | 5.66e-07 | 2.28e-07 | 6.57e-07 | 2.2283e-05 | 8.9764e-06 | 2.5866e-05
4120 | 5.67e-07 | 2.16e-07 | 6.96e-07 | 2.2323e-05 | 8.5039e-06 | 2.7402e-05
4160 | 5.66e-07 | 2.06e-07 | 7.24e-07 | 2.2283e-05 | 8.1102e-06 | 2.8504e-05
4200 | 5.66e-07 | 1.97e-07 | 7.45e-07 | 2.2283e-05 | 7.7559e-06 | 2.9331e-05
4240 | 5.65e-07 | 1.9e-07 | 7.62e-07 | 2.2244e-05 | 7.4803e-06 | 3e-05
4280 | 5.63e-07 | 1.84e-07 | 7.75e-07 | 2.2165e-05 | 7.2441e-06 | 3.0512e-05
4320 | 5.62e-07 | 1.8e-07 | 7.87e-07 | 2.2126e-05 | 7.0866e-06 | 3.0984e-05
4360 | 5.6e-07 | 1.76e-07 | 7.98e-07 | 2.2047e-05 | 6.9291e-06 | 3.1417e-05
4400 | 5.58e-07 | 1.73e-07 | 8.09e-07 | 2.1969e-05 | 6.811e-06 | 3.185e-05
4440 | 5.56e-07 | 1.71e-07 | 8.19e-07 | 2.189e-05 | 6.7323e-06 | 3.2244e-05
4480 | 5.54e-07 | 1.69e-07 | 8.29e-07 | 2.1811e-05 | 6.6535e-06 | 3.2638e-05
4520 | 5.51e-07 | 1.67e-07 | 8.39e-07 | 2.1693e-05 | 6.5748e-06 | 3.3031e-05
4560 | 5.49e-07 | 1.67e-07 | 8.5e-07 | 2.1614e-05 | 6.5748e-06 | 3.3465e-05
4600 | 5.47e-07 | 1.66e-07 | 8.6e-07 | 2.1535e-05 | 6.5354e-06 | 3.3858e-05
4640 | 5.45e-07 | 1.66e-07 | 8.7e-07 | 2.1457e-05 | 6.5354e-06 | 3.4252e-05
4680 | 5.42e-07 | 1.66e-07 | 8.79e-07 | 2.1339e-05 | 6.5354e-06 | 3.4606e-05
4720 | 5.4e-07 | 1.66e-07 | 8.88e-07 | 2.126e-05 | 6.5354e-06 | 3.4961e-05
4760 | 5.37e-07 | 1.67e-07 | 8.95e-07 | 2.1142e-05 | 6.5748e-06 | 3.5236e-05
4800 | 5.35e-07 | 1.68e-07 | 9.01e-07 | 2.1063e-05 | 6.6142e-06 | 3.5472e-05
(y) max | 5.67e-07 | 2.72e-07 | 9.01e-07 | 2.2323e-05 | 1.0709e-05 | 3.5472e-05
(y') max | 0.00021375 | 0.00010254 | 0.00033967 | 0.0084155 | 0.0040371 | 0.013373
Not noticeable to persons
Barely noticeable to persons
Easily noticeable to persons
No faults
Minor faults
Fault
Machine Curve
2880 rpm
3600 rpm
4320 rpm
Troublesome to persons
extremely mooth
very smooth
smooth
very good
good
fair
No faults
Minor faults
Faulty
Machine Curve
good
fair
extremely smooth
Vendor Limit = 2.54 mm/s
Industry Limit

## P3_UB
Point 3: At SW Corner
Upper Bound Soil
Pump Operating = 4215 rpm
Frequency (rpm) | Amplitude (m) |  |  | Amplitude (in)
| x | y | z | x | y | z
0 | 1.6946e-16 | 1.607e-17 | 5.112e-17 | 6.6717e-15 | 6.3268e-16 | 2.0126e-15
20 | 1.04e-09 | 1.365e-10 | 2.99e-10 | 4.0945e-08 | 5.374e-09 | 1.1772e-08
40 | 4.037e-09 | 5.29e-10 | 1.203e-09 | 1.5894e-07 | 2.0827e-08 | 4.7362e-08
60 | 9.07e-09 | 1.188e-09 | 2.719e-09 | 3.5709e-07 | 4.6772e-08 | 1.0705e-07
80 | 1.653e-08 | 2.173e-09 | 4.84e-09 | 6.5079e-07 | 8.5551e-08 | 1.9055e-07
100 | 2.605e-08 | 3.44e-09 | 7.64e-09 | 1.0256e-06 | 1.3543e-07 | 3.0079e-07
120 | 3.826e-08 | 5.07e-09 | 1.116e-08 | 1.5063e-06 | 1.9961e-07 | 4.3937e-07
140 | 5.33e-08 | 7.04e-09 | 1.55e-08 | 2.0984e-06 | 2.7717e-07 | 6.1024e-07
160 | 7.17e-08 | 9.42e-09 | 2.075e-08 | 2.8228e-06 | 3.7087e-07 | 8.1693e-07
180 | 9.4e-08 | 1.225e-08 | 2.72e-08 | 3.7008e-06 | 4.8228e-07 | 1.0709e-06
200 | 1.213e-07 | 1.557e-08 | 3.52e-08 | 4.7756e-06 | 6.1299e-07 | 1.3858e-06
220 | 1.542e-07 | 1.934e-08 | 4.51e-08 | 6.0709e-06 | 7.6142e-07 | 1.7756e-06
240 | 1.947e-07 | 2.353e-08 | 5.7e-08 | 7.6654e-06 | 9.2638e-07 | 2.2441e-06
260 | 2.405e-07 | 2.81e-08 | 7.11e-08 | 9.4685e-06 | 1.1063e-06 | 2.7992e-06
280 | 2.894e-07 | 3.26e-08 | 8.53e-08 | 1.1394e-05 | 1.2835e-06 | 3.3583e-06
300 | 3.37e-07 | 3.72e-08 | 9.76e-08 | 1.3268e-05 | 1.4646e-06 | 3.8425e-06
320 | 3.8e-07 | 4.25e-08 | 1.085e-07 | 1.4961e-05 | 1.6732e-06 | 4.2717e-06
340 | 4.26e-07 | 4.88e-08 | 1.186e-07 | 1.6772e-05 | 1.9213e-06 | 4.6693e-06
360 | 4.72e-07 | 5.63e-08 | 1.29e-07 | 1.8583e-05 | 2.2165e-06 | 5.0787e-06
380 | 5.22e-07 | 6.48e-08 | 1.404e-07 | 2.0551e-05 | 2.5512e-06 | 5.5276e-06
400 | 5.77e-07 | 7.36e-08 | 1.532e-07 | 2.2717e-05 | 2.8976e-06 | 6.0315e-06
420 | 6.35e-07 | 8.22e-08 | 1.673e-07 | 2.5e-05 | 3.2362e-06 | 6.5866e-06
440 | 6.98e-07 | 9.01e-08 | 1.842e-07 | 2.748e-05 | 3.5472e-06 | 7.252e-06
460 | 7.67e-07 | 9.7e-08 | 2.025e-07 | 3.0197e-05 | 3.8189e-06 | 7.9724e-06
480 | 8.437e-07 | 1.031e-07 | 2.241e-07 | 3.3217e-05 | 4.0591e-06 | 8.8228e-06
500 | 9.289e-07 | 1.087e-07 | 2.47e-07 | 3.6571e-05 | 4.2795e-06 | 9.7244e-06
520 | 1.0228e-06 | 1.137e-07 | 2.732e-07 | 4.0268e-05 | 4.4764e-06 | 1.0756e-05
540 | 1.1226e-06 | 1.183e-07 | 3.026e-07 | 4.4197e-05 | 4.6575e-06 | 1.1913e-05
560 | 1.2372e-06 | 1.224e-07 | 3.332e-07 | 4.8709e-05 | 4.8189e-06 | 1.3118e-05
580 | 1.3523e-06 | 1.262e-07 | 3.65e-07 | 5.324e-05 | 4.9685e-06 | 1.437e-05
600 | 1.458e-06 | 1.297e-07 | 3.99e-07 | 5.7402e-05 | 5.1063e-06 | 1.5709e-05
620 | 1.5738e-06 | 1.331e-07 | 4.312e-07 | 6.1961e-05 | 5.2402e-06 | 1.6976e-05
640 | 1.6601e-06 | 1.368e-07 | 4.614e-07 | 6.5358e-05 | 5.3858e-06 | 1.8165e-05
660 | 1.737e-06 | 1.414e-07 | 4.868e-07 | 6.8386e-05 | 5.5669e-06 | 1.9165e-05
680 | 1.7942e-06 | 1.479e-07 | 5.061e-07 | 7.0638e-05 | 5.8228e-06 | 1.9925e-05
700 | 1.8216e-06 | 1.555e-07 | 5.185e-07 | 7.1717e-05 | 6.122e-06 | 2.0413e-05
720 | 1.8092e-06 | 1.701e-07 | 5.209e-07 | 7.1228e-05 | 6.6969e-06 | 2.0508e-05
740 | 1.8071e-06 | 1.837e-07 | 5.242e-07 | 7.1146e-05 | 7.2323e-06 | 2.0638e-05
760 | 1.7952e-06 | 2.013e-07 | 5.22e-07 | 7.0677e-05 | 7.9252e-06 | 2.0551e-05
780 | 1.7936e-06 | 2.209e-07 | 5.2e-07 | 7.0614e-05 | 8.6969e-06 | 2.0472e-05
800 | 1.7922e-06 | 2.426e-07 | 5.14e-07 | 7.0559e-05 | 9.5512e-06 | 2.0236e-05
820 | 1.801e-06 | 2.663e-07 | 5.09e-07 | 7.0906e-05 | 1.0484e-05 | 2.0039e-05
840 | 1.83e-06 | 2.91e-07 | 5.03e-07 | 7.2047e-05 | 1.1457e-05 | 1.9803e-05
860 | 1.8592e-06 | 3.178e-07 | 4.98e-07 | 7.3197e-05 | 1.2512e-05 | 1.9606e-05
880 | 1.9084e-06 | 3.446e-07 | 4.93e-07 | 7.5134e-05 | 1.3567e-05 | 1.9409e-05
900 | 1.9678e-06 | 3.723e-07 | 4.88e-07 | 7.7472e-05 | 1.4657e-05 | 1.9213e-05
920 | 2.0372e-06 | 3.99e-07 | 4.85e-07 | 8.0205e-05 | 1.5709e-05 | 1.9094e-05
940 | 2.1066e-06 | 4.247e-07 | 4.82e-07 | 8.2937e-05 | 1.672e-05 | 1.8976e-05
960 | 2.176e-06 | 4.504e-07 | 4.82e-07 | 8.5669e-05 | 1.7732e-05 | 1.8976e-05
980 | 2.2454e-06 | 4.73e-07 | 4.81e-07 | 8.8402e-05 | 1.8622e-05 | 1.8937e-05
1000 | 2.3148e-06 | 4.925e-07 | 4.81e-07 | 9.1134e-05 | 1.939e-05 | 1.8937e-05
1020 | 2.3742e-06 | 5.1e-07 | 4.83e-07 | 9.3472e-05 | 2.0079e-05 | 1.9016e-05
1040 | 2.4337e-06 | 5.253e-07 | 4.86e-07 | 9.5815e-05 | 2.0681e-05 | 1.9134e-05
1060 | 2.4734e-06 | 5.376e-07 | 4.91e-07 | 9.7378e-05 | 2.1165e-05 | 1.9331e-05
1080 | 2.5134e-06 | 5.469e-07 | 4.96e-07 | 9.8953e-05 | 2.1531e-05 | 1.9528e-05
1100 | 2.5439e-06 | 5.541e-07 | 5.04e-07 | 0.00010015 | 2.1815e-05 | 1.9843e-05
1120 | 2.5649e-06 | 5.593e-07 | 5.14e-07 | 0.00010098 | 2.202e-05 | 2.0236e-05
1140 | 2.5864e-06 | 5.625e-07 | 5.25e-07 | 0.00010183 | 2.2146e-05 | 2.0669e-05
1160 | 2.5984e-06 | 5.638e-07 | 5.41e-07 | 0.0001023 | 2.2197e-05 | 2.1299e-05
1180 | 2.6009e-06 | 5.643e-07 | 5.61e-07 | 0.0001024 | 2.2217e-05 | 2.2087e-05
1200 | 2.6038e-06 | 5.648e-07 | 5.84e-07 | 0.00010251 | 2.2236e-05 | 2.2992e-05
1220 | 2.6069e-06 | 5.635e-07 | 6.12e-07 | 0.00010263 | 2.2185e-05 | 2.4094e-05
1240 | 2.6104e-06 | 5.622e-07 | 6.43e-07 | 0.00010277 | 2.2134e-05 | 2.5315e-05
1260 | 2.6042e-06 | 5.6e-07 | 6.79e-07 | 0.00010253 | 2.2047e-05 | 2.6732e-05
1280 | 2.5982e-06 | 5.576e-07 | 7.2e-07 | 0.00010229 | 2.1953e-05 | 2.8346e-05
1300 | 2.6022e-06 | 5.55e-07 | 7.64e-07 | 0.00010245 | 2.185e-05 | 3.0079e-05
1320 | 2.5959e-06 | 5.521e-07 | 8.06e-07 | 0.0001022 | 2.1736e-05 | 3.1732e-05
1340 | 2.589e-06 | 5.49e-07 | 8.44e-07 | 0.00010193 | 2.1614e-05 | 3.3228e-05
1360 | 2.5809e-06 | 5.451e-07 | 8.71e-07 | 0.00010161 | 2.1461e-05 | 3.4291e-05
1380 | 2.5716e-06 | 5.429e-07 | 8.82e-07 | 0.00010124 | 2.1374e-05 | 3.4724e-05
1400 | 2.5611e-06 | 5.414e-07 | 8.75e-07 | 0.00010083 | 2.1315e-05 | 3.4449e-05
1420 | 2.5497e-06 | 5.395e-07 | 8.52e-07 | 0.00010038 | 2.124e-05 | 3.3543e-05
1440 | 2.5379e-06 | 5.38e-07 | 8.2e-07 | 9.9917e-05 | 2.1181e-05 | 3.2283e-05
1460 | 2.5259e-06 | 5.375e-07 | 7.83e-07 | 9.9445e-05 | 2.1161e-05 | 3.0827e-05
1480 | 2.5139e-06 | 5.358e-07 | 7.49e-07 | 9.8972e-05 | 2.1094e-05 | 2.9488e-05
1500 | 2.5022e-06 | 5.348e-07 | 7.19e-07 | 9.8512e-05 | 2.1055e-05 | 2.8307e-05
1520 | 2.4906e-06 | 5.337e-07 | 6.93e-07 | 9.8055e-05 | 2.1012e-05 | 2.7283e-05
1540 | 2.4793e-06 | 5.325e-07 | 6.71e-07 | 9.761e-05 | 2.0965e-05 | 2.6417e-05
1560 | 2.4682e-06 | 5.311e-07 | 6.53e-07 | 9.7173e-05 | 2.0909e-05 | 2.5709e-05
1580 | 2.4673e-06 | 5.296e-07 | 6.39e-07 | 9.7138e-05 | 2.085e-05 | 2.5157e-05
1600 | 2.4564e-06 | 5.29e-07 | 6.28e-07 | 9.6709e-05 | 2.0827e-05 | 2.4724e-05
1620 | 2.4456e-06 | 5.274e-07 | 6.19e-07 | 9.6283e-05 | 2.0764e-05 | 2.437e-05
1640 | 2.4349e-06 | 5.257e-07 | 6.13e-07 | 9.5862e-05 | 2.0697e-05 | 2.4134e-05
1660 | 2.4341e-06 | 5.249e-07 | 6.09e-07 | 9.5831e-05 | 2.0665e-05 | 2.3976e-05
1680 | 2.4232e-06 | 5.23e-07 | 6.05e-07 | 9.5402e-05 | 2.0591e-05 | 2.3819e-05
1700 | 2.4124e-06 | 5.22e-07 | 6.03e-07 | 9.4976e-05 | 2.0551e-05 | 2.374e-05
1720 | 2.4016e-06 | 5.201e-07 | 6.02e-07 | 9.4551e-05 | 2.0476e-05 | 2.3701e-05
1740 | 2.4008e-06 | 5.181e-07 | 6.02e-07 | 9.452e-05 | 2.0398e-05 | 2.3701e-05
1760 | 2.39e-06 | 5.17e-07 | 6.01e-07 | 9.4094e-05 | 2.0354e-05 | 2.3661e-05
1780 | 2.3793e-06 | 5.15e-07 | 6.03e-07 | 9.3673e-05 | 2.0276e-05 | 2.374e-05
1800 | 2.3787e-06 | 5.139e-07 | 6.04e-07 | 9.365e-05 | 2.0232e-05 | 2.378e-05
1820 | 2.3681e-06 | 5.119e-07 | 6.05e-07 | 9.3232e-05 | 2.0154e-05 | 2.3819e-05
1840 | 2.3677e-06 | 5.108e-07 | 6.07e-07 | 9.3217e-05 | 2.011e-05 | 2.3898e-05
1860 | 2.3573e-06 | 5.098e-07 | 6.1e-07 | 9.2807e-05 | 2.0071e-05 | 2.4016e-05
1880 | 2.3569e-06 | 5.087e-07 | 6.13e-07 | 9.2791e-05 | 2.0028e-05 | 2.4134e-05
1900 | 2.3466e-06 | 5.077e-07 | 6.15e-07 | 9.2386e-05 | 1.9988e-05 | 2.4213e-05
1920 | 2.3464e-06 | 5.067e-07 | 6.19e-07 | 9.2378e-05 | 1.9949e-05 | 2.437e-05
1940 | 2.3362e-06 | 5.056e-07 | 6.22e-07 | 9.1976e-05 | 1.9906e-05 | 2.4488e-05
1960 | 2.3359e-06 | 5.046e-07 | 6.25e-07 | 9.1965e-05 | 1.9866e-05 | 2.4606e-05
1980 | 2.3357e-06 | 5.046e-07 | 6.29e-07 | 9.1957e-05 | 1.9866e-05 | 2.4764e-05
2000 | 2.3254e-06 | 5.036e-07 | 6.32e-07 | 9.1551e-05 | 1.9827e-05 | 2.4882e-05
2020 | 2.3252e-06 | 5.025e-07 | 6.35e-07 | 9.1543e-05 | 1.9783e-05 | 2.5e-05
2040 | 2.3249e-06 | 5.025e-07 | 6.39e-07 | 9.1531e-05 | 1.9783e-05 | 2.5157e-05
2060 | 2.3146e-06 | 5.014e-07 | 6.43e-07 | 9.1126e-05 | 1.974e-05 | 2.5315e-05
2080 | 2.3143e-06 | 5.014e-07 | 6.46e-07 | 9.1114e-05 | 1.974e-05 | 2.5433e-05
2100 | 2.314e-06 | 5.014e-07 | 6.5e-07 | 9.1102e-05 | 1.974e-05 | 2.5591e-05
2120 | 2.3137e-06 | 5.003e-07 | 6.53e-07 | 9.1091e-05 | 1.9697e-05 | 2.5709e-05
2140 | 2.3133e-06 | 5.002e-07 | 6.57e-07 | 9.1075e-05 | 1.9693e-05 | 2.5866e-05
2160 | 2.313e-06 | 5.002e-07 | 6.59e-07 | 9.1063e-05 | 1.9693e-05 | 2.5945e-05
2180 | 2.3027e-06 | 4.991e-07 | 6.63e-07 | 9.0657e-05 | 1.965e-05 | 2.6102e-05
2200 | 2.3024e-06 | 4.99e-07 | 6.67e-07 | 9.0646e-05 | 1.9646e-05 | 2.626e-05
2220 | 2.302e-06 | 4.98e-07 | 6.71e-07 | 9.063e-05 | 1.9606e-05 | 2.6417e-05
2240 | 2.3017e-06 | 4.979e-07 | 6.75e-07 | 9.0618e-05 | 1.9602e-05 | 2.6575e-05
2260 | 2.3014e-06 | 4.968e-07 | 6.79e-07 | 9.0606e-05 | 1.9559e-05 | 2.6732e-05
2280 | 2.3011e-06 | 4.967e-07 | 6.84e-07 | 9.0594e-05 | 1.9555e-05 | 2.6929e-05
2300 | 2.3008e-06 | 4.956e-07 | 6.9e-07 | 9.0583e-05 | 1.9512e-05 | 2.7165e-05
2320 | 2.3005e-06 | 4.945e-07 | 6.96e-07 | 9.0571e-05 | 1.9469e-05 | 2.7402e-05
2340 | 2.3002e-06 | 4.934e-07 | 7.02e-07 | 9.0559e-05 | 1.9425e-05 | 2.7638e-05
2360 | 2.29e-06 | 4.924e-07 | 7.09e-07 | 9.0157e-05 | 1.9386e-05 | 2.7913e-05
2380 | 2.2897e-06 | 4.913e-07 | 7.16e-07 | 9.0146e-05 | 1.9343e-05 | 2.8189e-05
2400 | 2.2895e-06 | 4.892e-07 | 7.24e-07 | 9.0138e-05 | 1.926e-05 | 2.8504e-05
(y) max | 2.6104e-06 | 5.648e-07 | 8.82e-07 | 0.00010277 | 2.2236e-05 | 3.4724e-05
(y') max | 0.0009841 | 0.00021292 | 0.00033251 | 0.038744 | 0.0083829 | 0.013091
Not noticeable to persons
Barely noticeable to persons
Easily noticeable to persons
No faults
Minor faults
Fault
Machine Curve
1424 rpm
1780 rpm
2136 rpm
Troublesome to persons
extremely mooth
very smooth
smooth
very good
good
fair
No faults
Minor faults
Faulty
Machine Curve
good
fair
extremely smooth
Vendor Limit = 0.7 mm/s
Industry Limit

## P4_UB
Point 4: At NW Corner
Upper Bound Soil
Pump Operating = 4215 rpm
Frequency (rpm) | Amplitude (m) |  |  | Amplitude (in)
| x | y | z | x | y | z
0 | 1.162e-16 | 1.607e-17 | 6.404e-17 | 4.5748e-15 | 6.3268e-16 | 2.5213e-15
20 | 8.13e-10 | 1.365e-10 | 3.378e-10 | 3.2008e-08 | 5.374e-09 | 1.3299e-08
40 | 3.31e-09 | 5.29e-10 | 1.355e-09 | 1.3031e-07 | 2.0827e-08 | 5.3346e-08
60 | 7.53e-09 | 1.188e-09 | 3.059e-09 | 2.9646e-07 | 4.6772e-08 | 1.2043e-07
80 | 1.36e-08 | 2.173e-09 | 5.46e-09 | 5.3543e-07 | 8.5551e-08 | 2.1496e-07
100 | 2.18e-08 | 3.44e-09 | 8.61e-09 | 8.5827e-07 | 1.3543e-07 | 3.3898e-07
120 | 3.23e-08 | 5.07e-09 | 1.256e-08 | 1.2717e-06 | 1.9961e-07 | 4.9449e-07
140 | 4.55e-08 | 7.04e-09 | 1.744e-08 | 1.7913e-06 | 2.7717e-07 | 6.8661e-07
160 | 6.21e-08 | 9.42e-09 | 2.33e-08 | 2.4449e-06 | 3.7087e-07 | 9.1732e-07
180 | 8.26e-08 | 1.225e-08 | 3.035e-08 | 3.252e-06 | 4.8228e-07 | 1.1949e-06
200 | 1.081e-07 | 1.557e-08 | 3.88e-08 | 4.2559e-06 | 6.1299e-07 | 1.5276e-06
220 | 1.392e-07 | 1.934e-08 | 4.9e-08 | 5.4803e-06 | 7.6142e-07 | 1.9291e-06
240 | 1.754e-07 | 2.353e-08 | 6.1e-08 | 6.9055e-06 | 9.2638e-07 | 2.4016e-06
260 | 2.146e-07 | 2.81e-08 | 7.44e-08 | 8.4488e-06 | 1.1063e-06 | 2.9291e-06
280 | 2.508e-07 | 3.26e-08 | 8.77e-08 | 9.874e-06 | 1.2835e-06 | 3.4528e-06
300 | 2.75e-07 | 3.72e-08 | 9.91e-08 | 1.0827e-05 | 1.4646e-06 | 3.9016e-06
320 | 2.95e-07 | 4.25e-08 | 1.095e-07 | 1.1614e-05 | 1.6732e-06 | 4.311e-06
340 | 3.16e-07 | 4.88e-08 | 1.197e-07 | 1.2441e-05 | 1.9213e-06 | 4.7126e-06
360 | 3.43e-07 | 5.63e-08 | 1.305e-07 | 1.3504e-05 | 2.2165e-06 | 5.1378e-06
380 | 3.77e-07 | 6.48e-08 | 1.426e-07 | 1.4843e-05 | 2.5512e-06 | 5.6142e-06
400 | 4.2e-07 | 7.36e-08 | 1.567e-07 | 1.6535e-05 | 2.8976e-06 | 6.1693e-06
420 | 4.69e-07 | 8.22e-08 | 1.718e-07 | 1.8465e-05 | 3.2362e-06 | 6.7638e-06
440 | 5.23e-07 | 9.01e-08 | 1.901e-07 | 2.0591e-05 | 3.5472e-06 | 7.4843e-06
460 | 5.82e-07 | 9.7e-08 | 2.105e-07 | 2.2913e-05 | 3.8189e-06 | 8.2874e-06
480 | 6.46e-07 | 1.031e-07 | 2.342e-07 | 2.5433e-05 | 4.0591e-06 | 9.2205e-06
500 | 7.17e-07 | 1.087e-07 | 2.621e-07 | 2.8228e-05 | 4.2795e-06 | 1.0319e-05
520 | 7.97e-07 | 1.137e-07 | 2.932e-07 | 3.1378e-05 | 4.4764e-06 | 1.1543e-05
540 | 8.86e-07 | 1.183e-07 | 3.275e-07 | 3.4882e-05 | 4.6575e-06 | 1.2894e-05
560 | 9.85e-07 | 1.224e-07 | 3.67e-07 | 3.878e-05 | 4.8189e-06 | 1.4449e-05
580 | 1.093e-06 | 1.262e-07 | 4.087e-07 | 4.3031e-05 | 4.9685e-06 | 1.6091e-05
600 | 1.208e-06 | 1.297e-07 | 4.547e-07 | 4.7559e-05 | 5.1063e-06 | 1.7902e-05
620 | 1.326e-06 | 1.331e-07 | 5.01e-07 | 5.2205e-05 | 5.2402e-06 | 1.9724e-05
640 | 1.444e-06 | 1.368e-07 | 5.476e-07 | 5.685e-05 | 5.3858e-06 | 2.1559e-05
660 | 1.553e-06 | 1.414e-07 | 5.904e-07 | 6.1142e-05 | 5.5669e-06 | 2.3244e-05
680 | 1.651e-06 | 1.479e-07 | 6.284e-07 | 6.5e-05 | 5.8228e-06 | 2.474e-05
700 | 1.73e-06 | 1.555e-07 | 6.595e-07 | 6.811e-05 | 6.122e-06 | 2.5965e-05
720 | 1.769e-06 | 1.701e-07 | 6.798e-07 | 6.9646e-05 | 6.6969e-06 | 2.6764e-05
740 | 1.808e-06 | 1.837e-07 | 6.991e-07 | 7.1181e-05 | 7.2323e-06 | 2.7524e-05
760 | 1.837e-06 | 2.013e-07 | 7.143e-07 | 7.2323e-05 | 7.9252e-06 | 2.8122e-05
780 | 1.856e-06 | 2.209e-07 | 7.255e-07 | 7.3071e-05 | 8.6969e-06 | 2.8563e-05
800 | 1.865e-06 | 2.426e-07 | 7.347e-07 | 7.3425e-05 | 9.5512e-06 | 2.8925e-05
820 | 1.864e-06 | 2.663e-07 | 7.439e-07 | 7.3386e-05 | 1.0484e-05 | 2.9287e-05
840 | 1.864e-06 | 2.91e-07 | 7.51e-07 | 7.3386e-05 | 1.1457e-05 | 2.9567e-05
860 | 1.863e-06 | 3.178e-07 | 7.591e-07 | 7.3346e-05 | 1.2512e-05 | 2.9886e-05
880 | 1.852e-06 | 3.446e-07 | 7.682e-07 | 7.2913e-05 | 1.3567e-05 | 3.0244e-05
900 | 1.842e-06 | 3.723e-07 | 7.773e-07 | 7.252e-05 | 1.4657e-05 | 3.0602e-05
920 | 1.822e-06 | 3.99e-07 | 7.875e-07 | 7.1732e-05 | 1.5709e-05 | 3.1004e-05
940 | 1.801e-06 | 4.247e-07 | 7.987e-07 | 7.0906e-05 | 1.672e-05 | 3.1445e-05
960 | 1.77e-06 | 4.504e-07 | 8.111e-07 | 6.9685e-05 | 1.7732e-05 | 3.1933e-05
980 | 1.73e-06 | 4.73e-07 | 8.245e-07 | 6.811e-05 | 1.8622e-05 | 3.2461e-05
1000 | 1.699e-06 | 4.925e-07 | 8.391e-07 | 6.689e-05 | 1.939e-05 | 3.3035e-05
1020 | 1.648e-06 | 5.1e-07 | 8.529e-07 | 6.4882e-05 | 2.0079e-05 | 3.3579e-05
1040 | 1.607e-06 | 5.253e-07 | 8.69e-07 | 6.3268e-05 | 2.0681e-05 | 3.4213e-05
1060 | 1.555e-06 | 5.376e-07 | 8.855e-07 | 6.122e-05 | 2.1165e-05 | 3.4862e-05
1080 | 1.504e-06 | 5.469e-07 | 9.026e-07 | 5.9213e-05 | 2.1531e-05 | 3.5535e-05
1100 | 1.452e-06 | 5.541e-07 | 9.203e-07 | 5.7165e-05 | 2.1815e-05 | 3.6232e-05
1120 | 1.4e-06 | 5.593e-07 | 9.386e-07 | 5.5118e-05 | 2.202e-05 | 3.6953e-05
1140 | 1.349e-06 | 5.625e-07 | 9.584e-07 | 5.311e-05 | 2.2146e-05 | 3.7732e-05
1160 | 1.297e-06 | 5.638e-07 | 9.789e-07 | 5.1063e-05 | 2.2197e-05 | 3.8539e-05
1180 | 1.255e-06 | 5.643e-07 | 9.987e-07 | 4.9409e-05 | 2.2217e-05 | 3.9319e-05
1200 | 1.203e-06 | 5.648e-07 | 1.0187e-06 | 4.7362e-05 | 2.2236e-05 | 4.0106e-05
1220 | 1.162e-06 | 5.635e-07 | 1.037e-06 | 4.5748e-05 | 2.2185e-05 | 4.0827e-05
1240 | 1.125e-06 | 5.622e-07 | 1.0512e-06 | 4.4291e-05 | 2.2134e-05 | 4.1386e-05
1260 | 1.087e-06 | 5.6e-07 | 1.0613e-06 | 4.2795e-05 | 2.2047e-05 | 4.1783e-05
1280 | 1.051e-06 | 5.576e-07 | 1.0619e-06 | 4.1378e-05 | 2.1953e-05 | 4.1807e-05
1300 | 1.017e-06 | 5.55e-07 | 1.0601e-06 | 4.0039e-05 | 2.185e-05 | 4.1736e-05
1320 | 9.85e-07 | 5.521e-07 | 1.0431e-06 | 3.878e-05 | 2.1736e-05 | 4.1067e-05
1340 | 9.57e-07 | 5.49e-07 | 1.078e-06 | 3.7677e-05 | 2.1614e-05 | 4.2441e-05
1360 | 9.3e-07 | 5.451e-07 | 1.1332e-06 | 3.6614e-05 | 2.1461e-05 | 4.4614e-05
1380 | 9.04e-07 | 5.429e-07 | 1.1866e-06 | 3.5591e-05 | 2.1374e-05 | 4.6717e-05
1400 | 8.81e-07 | 5.414e-07 | 1.224e-06 | 3.4685e-05 | 2.1315e-05 | 4.8189e-05
1420 | 8.57e-07 | 5.395e-07 | 1.265e-06 | 3.374e-05 | 2.124e-05 | 4.9803e-05
1440 | 8.32e-07 | 5.38e-07 | 1.298e-06 | 3.2756e-05 | 2.1181e-05 | 5.1102e-05
1460 | 8.1e-07 | 5.375e-07 | 1.326e-06 | 3.189e-05 | 2.1161e-05 | 5.2205e-05
1480 | 7.87e-07 | 5.358e-07 | 1.349e-06 | 3.0984e-05 | 2.1094e-05 | 5.311e-05
1500 | 7.67e-07 | 5.348e-07 | 1.359e-06 | 3.0197e-05 | 2.1055e-05 | 5.3504e-05
1520 | 7.47e-07 | 5.337e-07 | 1.379e-06 | 2.9409e-05 | 2.1012e-05 | 5.4291e-05
1540 | 7.28e-07 | 5.325e-07 | 1.397e-06 | 2.8661e-05 | 2.0965e-05 | 5.5e-05
1560 | 7.11e-07 | 5.311e-07 | 1.415e-06 | 2.7992e-05 | 2.0909e-05 | 5.5709e-05
1580 | 6.95e-07 | 5.296e-07 | 1.432e-06 | 2.7362e-05 | 2.085e-05 | 5.6378e-05
1600 | 6.79e-07 | 5.29e-07 | 1.45e-06 | 2.6732e-05 | 2.0827e-05 | 5.7087e-05
1620 | 6.63e-07 | 5.274e-07 | 1.468e-06 | 2.6102e-05 | 2.0764e-05 | 5.7795e-05
1640 | 6.47e-07 | 5.257e-07 | 1.486e-06 | 2.5472e-05 | 2.0697e-05 | 5.8504e-05
1660 | 6.33e-07 | 5.249e-07 | 1.504e-06 | 2.4921e-05 | 2.0665e-05 | 5.9213e-05
1680 | 6.19e-07 | 5.23e-07 | 1.522e-06 | 2.437e-05 | 2.0591e-05 | 5.9921e-05
1700 | 6.04e-07 | 5.22e-07 | 1.53e-06 | 2.378e-05 | 2.0551e-05 | 6.0236e-05
1720 | 5.91e-07 | 5.201e-07 | 1.548e-06 | 2.3268e-05 | 2.0476e-05 | 6.0945e-05
1740 | 5.77e-07 | 5.181e-07 | 1.567e-06 | 2.2717e-05 | 2.0398e-05 | 6.1693e-05
1760 | 5.66e-07 | 5.17e-07 | 1.586e-06 | 2.2283e-05 | 2.0354e-05 | 6.2441e-05
1780 | 5.53e-07 | 5.15e-07 | 1.604e-06 | 2.1772e-05 | 2.0276e-05 | 6.315e-05
1800 | 5.42e-07 | 5.139e-07 | 1.623e-06 | 2.1339e-05 | 2.0232e-05 | 6.3898e-05
1820 | 5.31e-07 | 5.119e-07 | 1.642e-06 | 2.0906e-05 | 2.0154e-05 | 6.4646e-05
1840 | 5.21e-07 | 5.108e-07 | 1.651e-06 | 2.0512e-05 | 2.011e-05 | 6.5e-05
1860 | 5.11e-07 | 5.098e-07 | 1.67e-06 | 2.0118e-05 | 2.0071e-05 | 6.5748e-05
1880 | 5.02e-07 | 5.087e-07 | 1.689e-06 | 1.9764e-05 | 2.0028e-05 | 6.6496e-05
1900 | 4.93e-07 | 5.077e-07 | 1.708e-06 | 1.9409e-05 | 1.9988e-05 | 6.7244e-05
1920 | 4.85e-07 | 5.067e-07 | 1.727e-06 | 1.9094e-05 | 1.9949e-05 | 6.7992e-05
1940 | 4.77e-07 | 5.056e-07 | 1.746e-06 | 1.878e-05 | 1.9906e-05 | 6.874e-05
1960 | 4.7e-07 | 5.046e-07 | 1.764e-06 | 1.8504e-05 | 1.9866e-05 | 6.9449e-05
1980 | 4.63e-07 | 5.046e-07 | 1.773e-06 | 1.8228e-05 | 1.9866e-05 | 6.9803e-05
2000 | 4.57e-07 | 5.036e-07 | 1.791e-06 | 1.7992e-05 | 1.9827e-05 | 7.0512e-05
2020 | 4.51e-07 | 5.025e-07 | 1.81e-06 | 1.7756e-05 | 1.9783e-05 | 7.126e-05
2040 | 4.45e-07 | 5.025e-07 | 1.828e-06 | 1.752e-05 | 1.9783e-05 | 7.1969e-05
2060 | 4.4e-07 | 5.014e-07 | 1.846e-06 | 1.7323e-05 | 1.974e-05 | 7.2677e-05
2080 | 4.35e-07 | 5.014e-07 | 1.865e-06 | 1.7126e-05 | 1.974e-05 | 7.3425e-05
2100 | 4.31e-07 | 5.014e-07 | 1.883e-06 | 1.6969e-05 | 1.974e-05 | 7.4134e-05
2120 | 4.26e-07 | 5.003e-07 | 1.901e-06 | 1.6772e-05 | 1.9697e-05 | 7.4843e-05
2140 | 4.22e-07 | 5.002e-07 | 1.919e-06 | 1.6614e-05 | 1.9693e-05 | 7.5551e-05
2160 | 4.18e-07 | 5.002e-07 | 1.948e-06 | 1.6457e-05 | 1.9693e-05 | 7.6693e-05
2180 | 4.13e-07 | 4.991e-07 | 1.966e-06 | 1.626e-05 | 1.965e-05 | 7.7402e-05
2200 | 4.09e-07 | 4.99e-07 | 1.985e-06 | 1.6102e-05 | 1.9646e-05 | 7.815e-05
2220 | 4.06e-07 | 4.98e-07 | 2.013e-06 | 1.5984e-05 | 1.9606e-05 | 7.9252e-05
2240 | 4.02e-07 | 4.979e-07 | 2.032e-06 | 1.5827e-05 | 1.9602e-05 | 8e-05
2260 | 3.97e-07 | 4.968e-07 | 2.061e-06 | 1.563e-05 | 1.9559e-05 | 8.1142e-05
2280 | 3.93e-07 | 4.967e-07 | 2.089e-06 | 1.5472e-05 | 1.9555e-05 | 8.2244e-05
2300 | 3.89e-07 | 4.956e-07 | 2.108e-06 | 1.5315e-05 | 1.9512e-05 | 8.2992e-05
2320 | 3.84e-07 | 4.945e-07 | 2.147e-06 | 1.5118e-05 | 1.9469e-05 | 8.4528e-05
2340 | 3.79e-07 | 4.934e-07 | 2.176e-06 | 1.4921e-05 | 1.9425e-05 | 8.5669e-05
2360 | 3.75e-07 | 4.924e-07 | 2.206e-06 | 1.4764e-05 | 1.9386e-05 | 8.685e-05
2380 | 3.69e-07 | 4.913e-07 | 2.245e-06 | 1.4528e-05 | 1.9343e-05 | 8.8386e-05
2400 | 3.64e-07 | 4.892e-07 | 2.284e-06 | 1.4331e-05 | 1.926e-05 | 8.9921e-05
(y) max | 1.865e-06 | 5.648e-07 | 2.284e-06 | 7.3425e-05 | 2.2236e-05 | 8.9921e-05
(y') max | 0.00070309 | 0.00021292 | 0.00086105 | 0.027681 | 0.0083829 | 0.0339
Not noticeable to persons
Barely noticeable to persons
Easily noticeable to persons
No faults
Minor faults
Fault
Machine Curve
1424 rpm
1780 rpm
2136 rpm
Troublesome to persons
extremely mooth
very smooth
smooth
very good
good
fair
No faults
Minor faults
Faulty
Machine Curve
good
fair
extremely smooth
Vendor Limit = 0.7 mm/s
Industry Limit

## P5_UB
Point 5: At NE Corner
Upper Bound Soil
Pump Operating = 4215 rpm
Frequency (rpm) | Amplitude (m) |  |  | Amplitude (in)
| x | y | z | x | y | z
0 | 1.162e-16 | 1.585e-17 | 6.404e-17 | 4.5748e-15 | 6.2402e-16 | 2.5213e-15
20 | 8.13e-10 | 1.367e-10 | 3.423e-10 | 3.2008e-08 | 5.3819e-09 | 1.3476e-08
40 | 3.31e-09 | 5.31e-10 | 1.385e-09 | 1.3031e-07 | 2.0906e-08 | 5.4528e-08
60 | 7.53e-09 | 1.193e-09 | 3.164e-09 | 2.9646e-07 | 4.6969e-08 | 1.2457e-07
80 | 1.36e-08 | 2.19e-09 | 5.7e-09 | 5.3543e-07 | 8.622e-08 | 2.2441e-07
100 | 2.18e-08 | 3.47e-09 | 9.07e-09 | 8.5827e-07 | 1.3661e-07 | 3.5709e-07
120 | 3.23e-08 | 5.13e-09 | 1.335e-08 | 1.2717e-06 | 2.0197e-07 | 5.2559e-07
140 | 4.55e-08 | 7.16e-09 | 1.86e-08 | 1.7913e-06 | 2.8189e-07 | 7.3228e-07
160 | 6.21e-08 | 9.64e-09 | 2.507e-08 | 2.4449e-06 | 3.7953e-07 | 9.8701e-07
180 | 8.26e-08 | 1.267e-08 | 3.27e-08 | 3.252e-06 | 4.9882e-07 | 1.2874e-06
200 | 1.081e-07 | 1.633e-08 | 4.19e-08 | 4.2559e-06 | 6.4291e-07 | 1.6496e-06
220 | 1.392e-07 | 2.071e-08 | 5.27e-08 | 5.4803e-06 | 8.1535e-07 | 2.0748e-06
240 | 1.754e-07 | 2.59e-08 | 6.53e-08 | 6.9055e-06 | 1.0197e-06 | 2.5709e-06
260 | 2.146e-07 | 3.18e-08 | 7.9e-08 | 8.4488e-06 | 1.252e-06 | 3.1102e-06
280 | 2.508e-07 | 3.82e-08 | 9.21e-08 | 9.874e-06 | 1.5039e-06 | 3.626e-06
300 | 2.75e-07 | 4.53e-08 | 1.031e-07 | 1.0827e-05 | 1.7835e-06 | 4.0591e-06
320 | 2.95e-07 | 5.29e-08 | 1.131e-07 | 1.1614e-05 | 2.0827e-06 | 4.4528e-06
340 | 3.16e-07 | 6.13e-08 | 1.23e-07 | 1.2441e-05 | 2.4134e-06 | 4.8425e-06
360 | 3.43e-07 | 7.04e-08 | 1.338e-07 | 1.3504e-05 | 2.7717e-06 | 5.2677e-06
380 | 3.77e-07 | 8e-08 | 1.447e-07 | 1.4843e-05 | 3.1496e-06 | 5.6969e-06
400 | 4.2e-07 | 8.98e-08 | 1.588e-07 | 1.6535e-05 | 3.5354e-06 | 6.252e-06
420 | 4.69e-07 | 9.93e-08 | 1.732e-07 | 1.8465e-05 | 3.9094e-06 | 6.8189e-06
440 | 5.23e-07 | 1.084e-07 | 1.9e-07 | 2.0591e-05 | 4.2677e-06 | 7.4803e-06
460 | 5.82e-07 | 1.173e-07 | 2.082e-07 | 2.2913e-05 | 4.6181e-06 | 8.1969e-06
480 | 6.46e-07 | 1.264e-07 | 2.279e-07 | 2.5433e-05 | 4.9764e-06 | 8.9724e-06
500 | 7.17e-07 | 1.362e-07 | 2.489e-07 | 2.8228e-05 | 5.3622e-06 | 9.7992e-06
520 | 7.97e-07 | 1.471e-07 | 2.723e-07 | 3.1378e-05 | 5.7913e-06 | 1.072e-05
540 | 8.86e-07 | 1.596e-07 | 2.959e-07 | 3.4882e-05 | 6.2835e-06 | 1.165e-05
560 | 9.85e-07 | 1.737e-07 | 3.188e-07 | 3.878e-05 | 6.8386e-06 | 1.2551e-05
580 | 1.093e-06 | 1.897e-07 | 3.417e-07 | 4.3031e-05 | 7.4685e-06 | 1.3453e-05
600 | 1.208e-06 | 2.078e-07 | 3.618e-07 | 4.7559e-05 | 8.1811e-06 | 1.4244e-05
620 | 1.326e-06 | 2.279e-07 | 3.779e-07 | 5.2205e-05 | 8.9724e-06 | 1.4878e-05
640 | 1.444e-06 | 2.499e-07 | 3.881e-07 | 5.685e-05 | 9.8386e-06 | 1.528e-05
660 | 1.553e-06 | 2.731e-07 | 3.91e-07 | 6.1142e-05 | 1.0752e-05 | 1.5394e-05
680 | 1.651e-06 | 2.993e-07 | 3.869e-07 | 6.5e-05 | 1.1783e-05 | 1.5232e-05
700 | 1.73e-06 | 3.255e-07 | 3.757e-07 | 6.811e-05 | 1.2815e-05 | 1.4791e-05
720 | 1.769e-06 | 3.538e-07 | 3.574e-07 | 6.9646e-05 | 1.3929e-05 | 1.4071e-05
740 | 1.808e-06 | 3.822e-07 | 3.388e-07 | 7.1181e-05 | 1.5047e-05 | 1.3339e-05
760 | 1.837e-06 | 4.096e-07 | 3.181e-07 | 7.2323e-05 | 1.6126e-05 | 1.2524e-05
780 | 1.856e-06 | 4.38e-07 | 2.972e-07 | 7.3071e-05 | 1.7244e-05 | 1.1701e-05
800 | 1.865e-06 | 4.665e-07 | 2.782e-07 | 7.3425e-05 | 1.8366e-05 | 1.0953e-05
820 | 1.864e-06 | 4.951e-07 | 2.611e-07 | 7.3386e-05 | 1.9492e-05 | 1.028e-05
840 | 1.864e-06 | 5.228e-07 | 2.469e-07 | 7.3386e-05 | 2.0583e-05 | 9.7205e-06
860 | 1.863e-06 | 5.505e-07 | 2.355e-07 | 7.3346e-05 | 2.1673e-05 | 9.2717e-06
880 | 1.852e-06 | 5.783e-07 | 2.282e-07 | 7.2913e-05 | 2.2768e-05 | 8.9843e-06
900 | 1.842e-06 | 6.042e-07 | 2.248e-07 | 7.252e-05 | 2.3787e-05 | 8.8504e-06
920 | 1.822e-06 | 6.292e-07 | 2.246e-07 | 7.1732e-05 | 2.4772e-05 | 8.8425e-06
940 | 1.801e-06 | 6.521e-07 | 2.266e-07 | 7.0906e-05 | 2.5673e-05 | 8.9213e-06
960 | 1.77e-06 | 6.731e-07 | 2.32e-07 | 6.9685e-05 | 2.65e-05 | 9.1339e-06
980 | 1.73e-06 | 6.911e-07 | 2.399e-07 | 6.811e-05 | 2.7209e-05 | 9.4449e-06
1000 | 1.699e-06 | 7.05e-07 | 2.497e-07 | 6.689e-05 | 2.7756e-05 | 9.8307e-06
1020 | 1.648e-06 | 7.168e-07 | 2.614e-07 | 6.4882e-05 | 2.822e-05 | 1.0291e-05
1040 | 1.607e-06 | 7.255e-07 | 2.763e-07 | 6.3268e-05 | 2.8563e-05 | 1.0878e-05
1060 | 1.555e-06 | 7.302e-07 | 2.935e-07 | 6.122e-05 | 2.8748e-05 | 1.1555e-05
1080 | 1.504e-06 | 7.338e-07 | 3.12e-07 | 5.9213e-05 | 2.889e-05 | 1.2283e-05
1100 | 1.452e-06 | 7.344e-07 | 3.341e-07 | 5.7165e-05 | 2.8913e-05 | 1.3154e-05
1120 | 1.4e-06 | 7.33e-07 | 3.579e-07 | 5.5118e-05 | 2.8858e-05 | 1.4091e-05
1140 | 1.349e-06 | 7.295e-07 | 3.856e-07 | 5.311e-05 | 2.872e-05 | 1.5181e-05
1160 | 1.297e-06 | 7.26e-07 | 4.149e-07 | 5.1063e-05 | 2.8583e-05 | 1.6335e-05
1180 | 1.255e-06 | 7.216e-07 | 4.49e-07 | 4.9409e-05 | 2.8409e-05 | 1.7677e-05
1200 | 1.203e-06 | 7.164e-07 | 4.87e-07 | 4.7362e-05 | 2.8205e-05 | 1.9173e-05
1220 | 1.162e-06 | 7.114e-07 | 5.29e-07 | 4.5748e-05 | 2.8008e-05 | 2.0827e-05
1240 | 1.125e-06 | 7.059e-07 | 5.78e-07 | 4.4291e-05 | 2.7791e-05 | 2.2756e-05
1260 | 1.087e-06 | 7.01e-07 | 6.35e-07 | 4.2795e-05 | 2.7598e-05 | 2.5e-05
1280 | 1.051e-06 | 6.979e-07 | 6.96e-07 | 4.1378e-05 | 2.7476e-05 | 2.7402e-05
1300 | 1.017e-06 | 6.944e-07 | 7.58e-07 | 4.0039e-05 | 2.7339e-05 | 2.9843e-05
1320 | 9.85e-07 | 6.915e-07 | 8.13e-07 | 3.878e-05 | 2.7224e-05 | 3.2008e-05
1340 | 9.57e-07 | 6.896e-07 | 8.58e-07 | 3.7677e-05 | 2.715e-05 | 3.378e-05
1360 | 9.3e-07 | 6.861e-07 | 8.9e-07 | 3.6614e-05 | 2.7012e-05 | 3.5039e-05
1380 | 9.04e-07 | 6.827e-07 | 9.07e-07 | 3.5591e-05 | 2.6878e-05 | 3.5709e-05
1400 | 8.81e-07 | 6.773e-07 | 9.11e-07 | 3.4685e-05 | 2.6665e-05 | 3.5866e-05
1420 | 8.57e-07 | 6.719e-07 | 9.06e-07 | 3.374e-05 | 2.6453e-05 | 3.5669e-05
1440 | 8.32e-07 | 6.65e-07 | 8.99e-07 | 3.2756e-05 | 2.6181e-05 | 3.5394e-05
1460 | 8.1e-07 | 6.578e-07 | 8.93e-07 | 3.189e-05 | 2.5898e-05 | 3.5157e-05
1480 | 7.87e-07 | 6.506e-07 | 8.88e-07 | 3.0984e-05 | 2.5614e-05 | 3.4961e-05
1500 | 7.67e-07 | 6.445e-07 | 8.88e-07 | 3.0197e-05 | 2.5374e-05 | 3.4961e-05
1520 | 7.47e-07 | 6.375e-07 | 8.9e-07 | 2.9409e-05 | 2.5098e-05 | 3.5039e-05
1540 | 7.28e-07 | 6.317e-07 | 8.96e-07 | 2.8661e-05 | 2.487e-05 | 3.5276e-05
1560 | 7.11e-07 | 6.261e-07 | 9.02e-07 | 2.7992e-05 | 2.465e-05 | 3.5512e-05
1580 | 6.95e-07 | 6.205e-07 | 9.11e-07 | 2.7362e-05 | 2.4429e-05 | 3.5866e-05
1600 | 6.79e-07 | 6.15e-07 | 9.2e-07 | 2.6732e-05 | 2.4213e-05 | 3.622e-05
1620 | 6.63e-07 | 6.106e-07 | 9.32e-07 | 2.6102e-05 | 2.4039e-05 | 3.6693e-05
1640 | 6.47e-07 | 6.052e-07 | 9.44e-07 | 2.5472e-05 | 2.3827e-05 | 3.7165e-05
1660 | 6.33e-07 | 5.998e-07 | 9.56e-07 | 2.4921e-05 | 2.3614e-05 | 3.7638e-05
1680 | 6.19e-07 | 5.954e-07 | 9.69e-07 | 2.437e-05 | 2.3441e-05 | 3.815e-05
1700 | 6.04e-07 | 5.9e-07 | 9.81e-07 | 2.378e-05 | 2.3228e-05 | 3.8622e-05
1720 | 5.91e-07 | 5.855e-07 | 9.93e-07 | 2.3268e-05 | 2.3051e-05 | 3.9094e-05
1740 | 5.77e-07 | 5.811e-07 | 1.007e-06 | 2.2717e-05 | 2.2878e-05 | 3.9646e-05
1760 | 5.66e-07 | 5.778e-07 | 1.019e-06 | 2.2283e-05 | 2.2748e-05 | 4.0118e-05
1780 | 5.53e-07 | 5.734e-07 | 1.033e-06 | 2.1772e-05 | 2.2575e-05 | 4.0669e-05
1800 | 5.42e-07 | 5.69e-07 | 1.046e-06 | 2.1339e-05 | 2.2402e-05 | 4.1181e-05
1820 | 5.31e-07 | 5.657e-07 | 1.059e-06 | 2.0906e-05 | 2.2272e-05 | 4.1693e-05
1840 | 5.21e-07 | 5.624e-07 | 1.073e-06 | 2.0512e-05 | 2.2142e-05 | 4.2244e-05
1860 | 5.11e-07 | 5.592e-07 | 1.087e-06 | 2.0118e-05 | 2.2016e-05 | 4.2795e-05
1880 | 5.02e-07 | 5.559e-07 | 1.1e-06 | 1.9764e-05 | 2.1886e-05 | 4.3307e-05
1900 | 4.93e-07 | 5.527e-07 | 1.114e-06 | 1.9409e-05 | 2.176e-05 | 4.3858e-05
1920 | 4.85e-07 | 5.505e-07 | 1.128e-06 | 1.9094e-05 | 2.1673e-05 | 4.4409e-05
1940 | 4.77e-07 | 5.483e-07 | 1.142e-06 | 1.878e-05 | 2.1587e-05 | 4.4961e-05
1960 | 4.7e-07 | 5.452e-07 | 1.155e-06 | 1.8504e-05 | 2.1465e-05 | 4.5472e-05
1980 | 4.63e-07 | 5.44e-07 | 1.174e-06 | 1.8228e-05 | 2.1417e-05 | 4.622e-05
2000 | 4.57e-07 | 5.419e-07 | 1.183e-06 | 1.7992e-05 | 2.1335e-05 | 4.6575e-05
2020 | 4.51e-07 | 5.407e-07 | 1.201e-06 | 1.7756e-05 | 2.1287e-05 | 4.7283e-05
2040 | 4.45e-07 | 5.396e-07 | 1.22e-06 | 1.752e-05 | 2.1244e-05 | 4.8031e-05
2060 | 4.4e-07 | 5.385e-07 | 1.229e-06 | 1.7323e-05 | 2.1201e-05 | 4.8386e-05
2080 | 4.35e-07 | 5.373e-07 | 1.247e-06 | 1.7126e-05 | 2.1154e-05 | 4.9094e-05
2100 | 4.31e-07 | 5.372e-07 | 1.266e-06 | 1.6969e-05 | 2.115e-05 | 4.9843e-05
2120 | 4.26e-07 | 5.371e-07 | 1.284e-06 | 1.6772e-05 | 2.1146e-05 | 5.0551e-05
2140 | 4.22e-07 | 5.369e-07 | 1.303e-06 | 1.6614e-05 | 2.1138e-05 | 5.1299e-05
2160 | 4.18e-07 | 5.368e-07 | 1.321e-06 | 1.6457e-05 | 2.1134e-05 | 5.2008e-05
2180 | 4.13e-07 | 5.377e-07 | 1.34e-06 | 1.626e-05 | 2.1169e-05 | 5.2756e-05
2200 | 4.09e-07 | 5.386e-07 | 1.368e-06 | 1.6102e-05 | 2.1205e-05 | 5.3858e-05
2220 | 4.06e-07 | 5.395e-07 | 1.387e-06 | 1.5984e-05 | 2.124e-05 | 5.4606e-05
2240 | 4.02e-07 | 5.403e-07 | 1.415e-06 | 1.5827e-05 | 2.1272e-05 | 5.5709e-05
2260 | 3.97e-07 | 5.412e-07 | 1.444e-06 | 1.563e-05 | 2.1307e-05 | 5.685e-05
2280 | 3.93e-07 | 5.421e-07 | 1.472e-06 | 1.5472e-05 | 2.1343e-05 | 5.7953e-05
2300 | 3.89e-07 | 5.43e-07 | 1.501e-06 | 1.5315e-05 | 2.1378e-05 | 5.9094e-05
2320 | 3.84e-07 | 5.449e-07 | 1.53e-06 | 1.5118e-05 | 2.1453e-05 | 6.0236e-05
2340 | 3.79e-07 | 5.458e-07 | 1.569e-06 | 1.4921e-05 | 2.1488e-05 | 6.1772e-05
2360 | 3.75e-07 | 5.477e-07 | 1.597e-06 | 1.4764e-05 | 2.1563e-05 | 6.2874e-05
2380 | 3.69e-07 | 5.485e-07 | 1.646e-06 | 1.4528e-05 | 2.1594e-05 | 6.4803e-05
2400 | 3.64e-07 | 5.494e-07 | 1.685e-06 | 1.4331e-05 | 2.163e-05 | 6.6339e-05
(y) max | 1.865e-06 | 7.344e-07 | 1.685e-06 | 7.3425e-05 | 2.8913e-05 | 6.6339e-05
(y') max | 0.00070309 | 0.00027686 | 0.00063523 | 0.027681 | 0.0109 | 0.025009
Not noticeable to persons
Barely noticeable to persons
Easily noticeable to persons
No faults
Minor faults
Fault
Machine Curve
1424 rpm
1780 rpm
2136 rpm
Troublesome to persons
extremely mooth
very smooth
smooth
very good
good
fair
No faults
Minor faults
Faulty
Machine Curve
good
fair
extremely smooth
Vendor Limit = 0.7 mm/s
Industry Limit

## P6_UB
Point 6: At SE Corner
Upper Bound Soil
Pump Operating = 4215 rpm
Frequency (rpm) | Amplitude (m) |  |  | Amplitude (in)
| x | y | z | x | y | z
0 | 1.6946e-16 | 1.585e-17 | 5.112e-17 | 6.6717e-15 | 6.2402e-16 | 2.0126e-15
20 | 1.04e-09 | 1.367e-10 | 3.03e-10 | 4.0945e-08 | 5.3819e-09 | 1.1929e-08
40 | 4.037e-09 | 5.31e-10 | 1.235e-09 | 1.5894e-07 | 2.0906e-08 | 4.8622e-08
60 | 9.07e-09 | 1.193e-09 | 2.82e-09 | 3.5709e-07 | 4.6969e-08 | 1.1102e-07
80 | 1.653e-08 | 2.19e-09 | 5.09e-09 | 6.5079e-07 | 8.622e-08 | 2.0039e-07
100 | 2.605e-08 | 3.47e-09 | 8.12e-09 | 1.0256e-06 | 1.3661e-07 | 3.1969e-07
120 | 3.826e-08 | 5.13e-09 | 1.194e-08 | 1.5063e-06 | 2.0197e-07 | 4.7008e-07
140 | 5.33e-08 | 7.16e-09 | 1.67e-08 | 2.0984e-06 | 2.8189e-07 | 6.5748e-07
160 | 7.17e-08 | 9.64e-09 | 2.239e-08 | 2.8228e-06 | 3.7953e-07 | 8.815e-07
180 | 9.4e-08 | 1.267e-08 | 2.91e-08 | 3.7008e-06 | 4.9882e-07 | 1.1457e-06
200 | 1.213e-07 | 1.633e-08 | 3.7e-08 | 4.7756e-06 | 6.4291e-07 | 1.4567e-06
220 | 1.542e-07 | 2.071e-08 | 4.62e-08 | 6.0709e-06 | 8.1535e-07 | 1.8189e-06
240 | 1.947e-07 | 2.59e-08 | 5.61e-08 | 7.6654e-06 | 1.0197e-06 | 2.2087e-06
260 | 2.405e-07 | 3.18e-08 | 6.62e-08 | 9.4685e-06 | 1.252e-06 | 2.6063e-06
280 | 2.894e-07 | 3.82e-08 | 7.49e-08 | 1.1394e-05 | 1.5039e-06 | 2.9488e-06
300 | 3.37e-07 | 4.53e-08 | 8.11e-08 | 1.3268e-05 | 1.7835e-06 | 3.1929e-06
320 | 3.8e-07 | 5.29e-08 | 8.67e-08 | 1.4961e-05 | 2.0827e-06 | 3.4134e-06
340 | 4.26e-07 | 6.13e-08 | 9.25e-08 | 1.6772e-05 | 2.4134e-06 | 3.6417e-06
360 | 4.72e-07 | 7.04e-08 | 9.99e-08 | 1.8583e-05 | 2.7717e-06 | 3.9331e-06
380 | 5.22e-07 | 8e-08 | 1.0894e-07 | 2.0551e-05 | 3.1496e-06 | 4.289e-06
400 | 5.77e-07 | 8.98e-08 | 1.2247e-07 | 2.2717e-05 | 3.5354e-06 | 4.8217e-06
420 | 6.35e-07 | 9.93e-08 | 1.4008e-07 | 2.5e-05 | 3.9094e-06 | 5.515e-06
440 | 6.98e-07 | 1.084e-07 | 1.623e-07 | 2.748e-05 | 4.2677e-06 | 6.3898e-06
460 | 7.67e-07 | 1.173e-07 | 1.861e-07 | 3.0197e-05 | 4.6181e-06 | 7.3268e-06
480 | 8.437e-07 | 1.264e-07 | 2.119e-07 | 3.3217e-05 | 4.9764e-06 | 8.3425e-06
500 | 9.289e-07 | 1.362e-07 | 2.406e-07 | 3.6571e-05 | 5.3622e-06 | 9.4724e-06
520 | 1.0228e-06 | 1.471e-07 | 2.713e-07 | 4.0268e-05 | 5.7913e-06 | 1.0681e-05
540 | 1.1226e-06 | 1.596e-07 | 3.04e-07 | 4.4197e-05 | 6.2835e-06 | 1.1969e-05
560 | 1.2372e-06 | 1.737e-07 | 3.386e-07 | 4.8709e-05 | 6.8386e-06 | 1.3331e-05
580 | 1.3523e-06 | 1.897e-07 | 3.742e-07 | 5.324e-05 | 7.4685e-06 | 1.4732e-05
600 | 1.458e-06 | 2.078e-07 | 4.108e-07 | 5.7402e-05 | 8.1811e-06 | 1.6173e-05
620 | 1.5738e-06 | 2.279e-07 | 4.453e-07 | 6.1961e-05 | 8.9724e-06 | 1.7531e-05
640 | 1.6601e-06 | 2.499e-07 | 4.766e-07 | 6.5358e-05 | 9.8386e-06 | 1.8764e-05
660 | 1.737e-06 | 2.731e-07 | 5.029e-07 | 6.8386e-05 | 1.0752e-05 | 1.9799e-05
680 | 1.7942e-06 | 2.993e-07 | 5.231e-07 | 7.0638e-05 | 1.1783e-05 | 2.0594e-05
700 | 1.8216e-06 | 3.255e-07 | 5.351e-07 | 7.1717e-05 | 1.2815e-05 | 2.1067e-05
720 | 1.8092e-06 | 3.538e-07 | 5.37e-07 | 7.1228e-05 | 1.3929e-05 | 2.1142e-05
740 | 1.8071e-06 | 3.822e-07 | 5.397e-07 | 7.1146e-05 | 1.5047e-05 | 2.1248e-05
760 | 1.7952e-06 | 4.096e-07 | 5.384e-07 | 7.0677e-05 | 1.6126e-05 | 2.1197e-05
780 | 1.7936e-06 | 4.38e-07 | 5.34e-07 | 7.0614e-05 | 1.7244e-05 | 2.1024e-05
800 | 1.7922e-06 | 4.665e-07 | 5.296e-07 | 7.0559e-05 | 1.8366e-05 | 2.085e-05
820 | 1.801e-06 | 4.951e-07 | 5.253e-07 | 7.0906e-05 | 1.9492e-05 | 2.0681e-05
840 | 1.83e-06 | 5.228e-07 | 5.211e-07 | 7.2047e-05 | 2.0583e-05 | 2.0516e-05
860 | 1.8592e-06 | 5.505e-07 | 5.17e-07 | 7.3197e-05 | 2.1673e-05 | 2.0354e-05
880 | 1.9084e-06 | 5.783e-07 | 5.15e-07 | 7.5134e-05 | 2.2768e-05 | 2.0276e-05
900 | 1.9678e-06 | 6.042e-07 | 5.143e-07 | 7.7472e-05 | 2.3787e-05 | 2.0248e-05
920 | 2.0372e-06 | 6.292e-07 | 5.159e-07 | 8.0205e-05 | 2.4772e-05 | 2.0311e-05
940 | 2.1066e-06 | 6.521e-07 | 5.179e-07 | 8.2937e-05 | 2.5673e-05 | 2.039e-05
960 | 2.176e-06 | 6.731e-07 | 5.223e-07 | 8.5669e-05 | 2.65e-05 | 2.0563e-05
980 | 2.2454e-06 | 6.911e-07 | 5.27e-07 | 8.8402e-05 | 2.7209e-05 | 2.0748e-05
1000 | 2.3148e-06 | 7.05e-07 | 5.34e-07 | 9.1134e-05 | 2.7756e-05 | 2.1024e-05
1020 | 2.3742e-06 | 7.168e-07 | 5.41e-07 | 9.3472e-05 | 2.822e-05 | 2.1299e-05
1040 | 2.4337e-06 | 7.255e-07 | 5.51e-07 | 9.5815e-05 | 2.8563e-05 | 2.1693e-05
1060 | 2.4734e-06 | 7.302e-07 | 5.61e-07 | 9.7378e-05 | 2.8748e-05 | 2.2087e-05
1080 | 2.5134e-06 | 7.338e-07 | 5.74e-07 | 9.8953e-05 | 2.889e-05 | 2.2598e-05
1100 | 2.5439e-06 | 7.344e-07 | 5.88e-07 | 0.00010015 | 2.8913e-05 | 2.315e-05
1120 | 2.5649e-06 | 7.33e-07 | 6.02e-07 | 0.00010098 | 2.8858e-05 | 2.3701e-05
1140 | 2.5864e-06 | 7.295e-07 | 6.2e-07 | 0.00010183 | 2.872e-05 | 2.4409e-05
1160 | 2.5984e-06 | 7.26e-07 | 6.4e-07 | 0.0001023 | 2.8583e-05 | 2.5197e-05
1180 | 2.6009e-06 | 7.216e-07 | 6.63e-07 | 0.0001024 | 2.8409e-05 | 2.6102e-05
1200 | 2.6038e-06 | 7.164e-07 | 6.87e-07 | 0.00010251 | 2.8205e-05 | 2.7047e-05
1220 | 2.6069e-06 | 7.114e-07 | 7.17e-07 | 0.00010263 | 2.8008e-05 | 2.8228e-05
1240 | 2.6104e-06 | 7.059e-07 | 7.51e-07 | 0.00010277 | 2.7791e-05 | 2.9567e-05
1260 | 2.6042e-06 | 7.01e-07 | 7.89e-07 | 0.00010253 | 2.7598e-05 | 3.1063e-05
1280 | 2.5982e-06 | 6.979e-07 | 8.33e-07 | 0.00010229 | 2.7476e-05 | 3.2795e-05
1300 | 2.6022e-06 | 6.944e-07 | 8.79e-07 | 0.00010245 | 2.7339e-05 | 3.4606e-05
1320 | 2.5959e-06 | 6.915e-07 | 9.27e-07 | 0.0001022 | 2.7224e-05 | 3.6496e-05
1340 | 2.589e-06 | 6.896e-07 | 9.75e-07 | 0.00010193 | 2.715e-05 | 3.8386e-05
1360 | 2.5809e-06 | 6.861e-07 | 1.017e-06 | 0.00010161 | 2.7012e-05 | 4.0039e-05
1380 | 2.5716e-06 | 6.827e-07 | 1.049e-06 | 0.00010124 | 2.6878e-05 | 4.1299e-05
1400 | 2.5611e-06 | 6.773e-07 | 1.066e-06 | 0.00010083 | 2.6665e-05 | 4.1969e-05
1420 | 2.5497e-06 | 6.719e-07 | 1.069e-06 | 0.00010038 | 2.6453e-05 | 4.2087e-05
1440 | 2.5379e-06 | 6.65e-07 | 1.059e-06 | 9.9917e-05 | 2.6181e-05 | 4.1693e-05
1460 | 2.5259e-06 | 6.578e-07 | 1.044e-06 | 9.9445e-05 | 2.5898e-05 | 4.1102e-05
1480 | 2.5139e-06 | 6.506e-07 | 1.024e-06 | 9.8972e-05 | 2.5614e-05 | 4.0315e-05
1500 | 2.5022e-06 | 6.445e-07 | 1.004e-06 | 9.8512e-05 | 2.5374e-05 | 3.9528e-05
1520 | 2.4906e-06 | 6.375e-07 | 9.87e-07 | 9.8055e-05 | 2.5098e-05 | 3.8858e-05
1540 | 2.4793e-06 | 6.317e-07 | 9.71e-07 | 9.761e-05 | 2.487e-05 | 3.8228e-05
1560 | 2.4682e-06 | 6.261e-07 | 9.57e-07 | 9.7173e-05 | 2.465e-05 | 3.7677e-05
1580 | 2.4673e-06 | 6.205e-07 | 9.45e-07 | 9.7138e-05 | 2.4429e-05 | 3.7205e-05
1600 | 2.4564e-06 | 6.15e-07 | 9.34e-07 | 9.6709e-05 | 2.4213e-05 | 3.6772e-05
1620 | 2.4456e-06 | 6.106e-07 | 9.25e-07 | 9.6283e-05 | 2.4039e-05 | 3.6417e-05
1640 | 2.4349e-06 | 6.052e-07 | 9.18e-07 | 9.5862e-05 | 2.3827e-05 | 3.6142e-05
1660 | 2.4341e-06 | 5.998e-07 | 9.11e-07 | 9.5831e-05 | 2.3614e-05 | 3.5866e-05
1680 | 2.4232e-06 | 5.954e-07 | 9.06e-07 | 9.5402e-05 | 2.3441e-05 | 3.5669e-05
1700 | 2.4124e-06 | 5.9e-07 | 9.01e-07 | 9.4976e-05 | 2.3228e-05 | 3.5472e-05
1720 | 2.4016e-06 | 5.855e-07 | 8.97e-07 | 9.4551e-05 | 2.3051e-05 | 3.5315e-05
1740 | 2.4008e-06 | 5.811e-07 | 8.93e-07 | 9.452e-05 | 2.2878e-05 | 3.5157e-05
1760 | 2.39e-06 | 5.778e-07 | 8.88e-07 | 9.4094e-05 | 2.2748e-05 | 3.4961e-05
1780 | 2.3793e-06 | 5.734e-07 | 8.85e-07 | 9.3673e-05 | 2.2575e-05 | 3.4843e-05
1800 | 2.3787e-06 | 5.69e-07 | 8.83e-07 | 9.365e-05 | 2.2402e-05 | 3.4764e-05
1820 | 2.3681e-06 | 5.657e-07 | 8.79e-07 | 9.3232e-05 | 2.2272e-05 | 3.4606e-05
1840 | 2.3677e-06 | 5.624e-07 | 8.76e-07 | 9.3217e-05 | 2.2142e-05 | 3.4488e-05
1860 | 2.3573e-06 | 5.592e-07 | 8.73e-07 | 9.2807e-05 | 2.2016e-05 | 3.437e-05
1880 | 2.3569e-06 | 5.559e-07 | 8.7e-07 | 9.2791e-05 | 2.1886e-05 | 3.4252e-05
1900 | 2.3466e-06 | 5.527e-07 | 8.68e-07 | 9.2386e-05 | 2.176e-05 | 3.4173e-05
1920 | 2.3464e-06 | 5.505e-07 | 8.65e-07 | 9.2378e-05 | 2.1673e-05 | 3.4055e-05
1940 | 2.3362e-06 | 5.483e-07 | 8.62e-07 | 9.1976e-05 | 2.1587e-05 | 3.3937e-05
1960 | 2.3359e-06 | 5.452e-07 | 8.58e-07 | 9.1965e-05 | 2.1465e-05 | 3.378e-05
1980 | 2.3357e-06 | 5.44e-07 | 8.55e-07 | 9.1957e-05 | 2.1417e-05 | 3.3661e-05
2000 | 2.3254e-06 | 5.419e-07 | 8.51e-07 | 9.1551e-05 | 2.1335e-05 | 3.3504e-05
2020 | 2.3252e-06 | 5.407e-07 | 8.47e-07 | 9.1543e-05 | 2.1287e-05 | 3.3346e-05
2040 | 2.3249e-06 | 5.396e-07 | 8.43e-07 | 9.1531e-05 | 2.1244e-05 | 3.3189e-05
2060 | 2.3146e-06 | 5.385e-07 | 8.38e-07 | 9.1126e-05 | 2.1201e-05 | 3.2992e-05
2080 | 2.3143e-06 | 5.373e-07 | 8.34e-07 | 9.1114e-05 | 2.1154e-05 | 3.2835e-05
2100 | 2.314e-06 | 5.372e-07 | 8.29e-07 | 9.1102e-05 | 2.115e-05 | 3.2638e-05
2120 | 2.3137e-06 | 5.371e-07 | 8.25e-07 | 9.1091e-05 | 2.1146e-05 | 3.248e-05
2140 | 2.3133e-06 | 5.369e-07 | 8.2e-07 | 9.1075e-05 | 2.1138e-05 | 3.2283e-05
2160 | 2.313e-06 | 5.368e-07 | 8.16e-07 | 9.1063e-05 | 2.1134e-05 | 3.2126e-05
2180 | 2.3027e-06 | 5.377e-07 | 8.11e-07 | 9.0657e-05 | 2.1169e-05 | 3.1929e-05
2200 | 2.3024e-06 | 5.386e-07 | 8.06e-07 | 9.0646e-05 | 2.1205e-05 | 3.1732e-05
2220 | 2.302e-06 | 5.395e-07 | 8.02e-07 | 9.063e-05 | 2.124e-05 | 3.1575e-05
2240 | 2.3017e-06 | 5.403e-07 | 7.97e-07 | 9.0618e-05 | 2.1272e-05 | 3.1378e-05
2260 | 2.3014e-06 | 5.412e-07 | 7.93e-07 | 9.0606e-05 | 2.1307e-05 | 3.122e-05
2280 | 2.3011e-06 | 5.421e-07 | 7.9e-07 | 9.0594e-05 | 2.1343e-05 | 3.1102e-05
2300 | 2.3008e-06 | 5.43e-07 | 7.86e-07 | 9.0583e-05 | 2.1378e-05 | 3.0945e-05
2320 | 2.3005e-06 | 5.449e-07 | 7.84e-07 | 9.0571e-05 | 2.1453e-05 | 3.0866e-05
2340 | 2.3002e-06 | 5.458e-07 | 7.81e-07 | 9.0559e-05 | 2.1488e-05 | 3.0748e-05
2360 | 2.29e-06 | 5.477e-07 | 7.8e-07 | 9.0157e-05 | 2.1563e-05 | 3.0709e-05
2380 | 2.2897e-06 | 5.485e-07 | 7.8e-07 | 9.0146e-05 | 2.1594e-05 | 3.0709e-05
2400 | 2.2895e-06 | 5.494e-07 | 7.81e-07 | 9.0138e-05 | 2.163e-05 | 3.0748e-05
(y) max | 2.6104e-06 | 7.344e-07 | 1.069e-06 | 0.00010277 | 2.8913e-05 | 4.2087e-05
(y') max | 0.0009841 | 0.00027686 | 0.000403 | 0.038744 | 0.0109 | 0.015866
Not noticeable to persons
Barely noticeable to persons
Easily noticeable to persons
No faults
Minor faults
Fault
Machine Curve
1424 rpm
1780 rpm
2136 rpm
Troublesome to persons
extremely mooth
very smooth
smooth
very good
good
fair
No faults
Minor faults
Faulty
Machine Curve
good
fair
extremely smooth
Vendor Limit = 0.7 mm/s
Industry Limit